## Calculator
Series / Parallel Calculator with "Auto Plot"
Joe Evans, Ph.D 5/20/06 Hydromatic Western Region Manager
www.pumped101.com
Follow the steps below to compare similar or identical pumps operating in series or parallel.
Scroll down to row 47 for more detailed instructions and comments on the included example.
1) Enter up to eight* "common" flows (Q) in cells D22 - K22
2) Enter corresponding heads (H) for the higher pressure pump (Pump 1) in cells D24 - K24
3) Enter the corresponding heads for Pump 2 (or the static pressure) in cells D26 - K26
4) Enter the head values for the system curve (if desired) in cells D28 - K28. See the instructions Step 4 below for the entry of parallel values.
5) Click on the Series, Parallel Identical, or Parallel Similar tabs to view the results
FLOW / HEAD | Q1 / H1 | Q2 / H2 | Q3 / H3 | Q4 / H4 | Q5 / H5 | Q6 / H6 | Q7 / H7 | Q8 / H8
FLOW | 0 | 100 | 200 | 300 | 400 | 500 | 600 | 700
HEAD PUMP 1 | 145 | 138 | 130 | 123 | 114 | 102 | 90 | 75
HEAD PUMP 2 | 122 | 114 | 105 | 97 | 88 | 77 | 65 | 50
SYS CURVE (SER) | 155 | 155 | 157 | 160 | 163 | 166 | 169 | 172
SYS CURVE (PAR) | 80 | 83 | 86 | 89 | 91 | 94 | 97 | 100
Sys Flow Parallel | 0 | 200 | 400 | 600 | 800 | 1000 | 1200 | 1400
Pumps In Series
Series Head | 267 | 252 | 235 | 220 | 202 | 179 | 155 | 125
Series Flow | 0 | 100 | 200 | 300 | 400 | 500 | 600 | 700
Pumps In Parallel
Identical Pumps (P1)
Parallel Head | 145 | 138 | 130 | 123 | 114 | 102 | 90 | 75
Parallel Flow | 0 | 200 | 400 | 600 | 800 | 1000 | 1200 | 1400
Similar Pumps (P1 & P2)
Parallel Head | 122 | 114 | 105 | 97 | 88 | 77 | 65 | 50
Parallel Flow | 305.9742 | 491.2024 | 685.5099 | 844.9617 | 1009.402 | 1188.869 | 1357.6172 | 1528.8106
Series / Parallel Calculator Instructions
The Series / Parallel Calculator allows you to view the performance of two pumps when operating in series or
parallel. In the case of series operation, the plot may be of two pumps or one pump and the existing static
pressure at its suction. In the case of parallel operation, you can view the performance of two identical pumps
or two pumps of similar flow but differing heads. The plots generated for pumps operating in series and identical
pumps operating in parallel are exact. By exact, I mean that the generated curve is a direct result of the two
curves that were entered. The plot generated for similar pumps operating in parallel is a close approximation
of their actual performance. You will note that the final point on the resulting curve will often exceed the sum of
the two maximum flows for the curves entered. This anomaly occurs due to the method used by xcel to calculate
the resulting flows and heads of similar pumps. It is explained in detail in the "Example" section below.
Step 1
Enter up to eight flow points that are common to both pumps in D22 - K22. If you want to enter fewer that eight
points, you must duplicate the last flow entered. For example if the maximum flow of 500 gpm is entered in Q6
then reenter it in Q7 and Q8.
Step 2
Enter the corresponding heads produced by Pump 1 for each flow point previously entered. Regardless of the
application (serial or parallel) Pump 1 is the one that produces the highest head. If fewer than eight points
are entered follow the same rule for flow in step 1 - - duplicate the last value entered.
Step 3
Enter the corresponding heads produced by Pump 2 for each of the flow points. In the case where Pump 1 is a
booster pump that is boosting existing pipeline pressure, enter the pipeline static pressure for each point. These
pressure values may or may not be the same for each flow point - - it will depend upon the capability of the pipeline.
If fewer than eight points are entered follow the rule in step 3.
Step 4
Enter the corresponding heads for the optional system curve. Since parallel operation could double the flow, each
point of Q will be double that entered in Step 1. For example if E22 is 100 then E30 will be 200 and so on. Flows
for the series system curve are the same as the pump flows entered earlier since series flow remains the same.
Step 5
Click on the appropriate tab (Series, Parallel Identical, Parallel Similar) to view your results. The "Parallel Identical"
tab will always show the results for the data entered for Pump 1. Please note that some pumps used in series
may not be compatible with parallel operation so the results in the parallel tabs may be skewed.
The tabs labeled "high gauss" and "low gauss" are used to calculate parallel flows and should not be changed.
About the Example
The example included with the calculator was chosen to illustrate all three applications. The pumps have common
flows of 0 to 700 gpm but produce different heads at each capacity point. The Series tab shows that the resulting
head at each flow point is the sum of the heads produced by the pumps at each point. The Parallel Identical tab
shows the result when two "Pump 1" pumps are operated in parallel. As expected the resulting flow is the sum
of the flows at each head / capacity point. The Parallel Similar tab approximates the result when Pumps 1 and 2
are operated in parallel. You will note that Pump 2 does not begin to contribute to the flow until the head of
Pump 1 drops below 122 feet. At 77' Pump 1 contributes a little less than 700 gpm while Pump 2 adds about
500 gpm. The combined flow as shown by the red curve is 1189 gpm. The maximum calculated flow of
1529 gpm at 50' is obtained by extrapolating the flow of Pump 1 to its expected value at 50'.

## high gauss
| x | y | x^2 | x^3 | x^4 | x^5 | x^6 | xy | x^2y | x^3y
1 | 145 | 0 | 21025 | 3048625 | 442050625 | 64097340625 | 9294114390625 | 0 | 0 | 0 | 1 |  |  |  |  | 8 | 917 | 109223 | 13428191 | 2800 |  |  | 0 | 100 | 200 | 300 | 400 | 500 | 600 | 700
2 | 138 | 100 | 19044 | 2628072 | 362673936 | 50049003168 | 6906762437184 | 13800 | 1904400 | 262807200 | 2 |  |  |  |  | 917 | 109223 | 13428191 | 1693611059 | 279800
3 | 130 | 200 | 16900 | 2197000 | 285610000 | 37129300000 | 4826809000000 | 26000 | 3380000 | 439400000 | 3 |  |  |  |  | 109223 | 13428191 | 1693611059 | 218001601367 | 29021000 |  |  | 145 | 138 | 130 | 123 | 114 | 102 | 90 | 75
4 | 123 | 300 | 15129 | 1860867 | 228886641 | 28153056843 | 3462825991689 | 36900 | 4538700 | 558260100 | 4 |  |  |  |  | 13428191 | 1693611059 | 218001601367 | 28521066378323 | 3116401400
5 | 114 | 400 | 12996 | 1481544 | 168896016 | 19254145824 | 2194972623936 | 45600 | 5198400 | 592617600 | 5
6 | 102 | 500 | 10404 | 1061208 | 108243216 | 11040808032 | 1126162419264 | 51000 | 5202000 | 530604000 | 6 |  |  |  |  | 1 | 114.625 | 13652.875 | 1678523.875 | 350
7 | 90 | 600 | 8100 | 729000 | 65610000 | 5904900000 | 531441000000 | 54000 | 4860000 | 437400000 | 7 | X | Y |  |  | 0 | 4111.875 | 908504.625 | 154404665.625 | -41150
8 | 75 | 700 | 5625 | 421875 | 31640625 | 2373046875 | 177978515625 | 52500 | 3937500 | 295312500 | 8 | 122 | 305.9742 | n= | 8 | 0 | 908504.625 | 202403092.875 | 34668188167.875 | -9207050 |  | constants in column x | 122 | 114 | 105 | 97 | 88 | 77 | 65 | 50
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 392.5457 | sum(x) | 917 | 0 | 154404665.625 | 34668188167.875 | 5.9815e+12 | -1583465450
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 478.9355 | sum(x^2) | 109223
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 546.9654 | sum(x^3) | 13428191
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 614.836 | sum(x^4) | 1693611059 | 1 | 0 | -11673.1241 | -2625749.6735 | 1497.1211
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 687.1795 | sum(x^5) | 218001601367 | 0 | 1 | 220.9466 | 37550.9143 | -10.0076
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 755.4383 | sum(x^6) | 28521066378323 | 0 | 0 | 1672123.756 | 553008878.1614 | -115099.1701
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 829.7328 | sum(y) | 2800 | 0 | 0 | 553008878.1614 | 183490824575.7812 | -38245327.679
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0744 | 1047.4431 | sum(xy) | 279800
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1949 | 1046.8081 | sum(x^2y) | 29021000 | 1 | 0 | 0 | 1234814.6253 | 693.6119
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3639 | 1045.9191 | sum(x^3y) | 3116401400 | 0 | 1 | 0 | -35521.0742 | 5.2011
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5349 | 1045.0205 |  |  | 0 | 0 | 1 | 330.7225 | -0.068834
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7386 | 1043.9526 |  |  | 0 | 0 | 0 | 598369255.4091 | -179447.2677
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9136 | 1043.0371
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9417 | 1042.8904 |  |  | ^b1 | ^b2 | ^b3 | ^b4 | ^Results
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 0 | 0 | 0 | 1063.9252
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1 | 0 | 0 | -5.4515 | X
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1 | 0 | 0.030348 | X^2
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 1 | -0.00029989 | X^3
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## low gauss
| x | y | x^2 | x^3 | x^4 | x^5 | x^6 | xy | x^2y | x^3y
1 | 122 | 0 | 14884 | 1815848 | 221533456 | 27027081632 | 3297303959104 | 0 | 0 | 0 | 1 |  |  |  |  | 8 | 718 | 68712 | 6905320 | 2800 |  |  |  | 0 | 100 | 200 | 300 | 400 | 500 | 600 | 700
2 | 114 | 100 | 12996 | 1481544 | 168896016 | 19254145824 | 2194972623936 | 11400 | 1299600 | 148154400 | 2 |  |  |  |  | 718 | 68712 | 6905320 | 719732580 | 209200
3 | 105 | 200 | 11025 | 1157625 | 121550625 | 12762815625 | 1340095640625 | 21000 | 2205000 | 231525000 | 3 |  |  |  |  | 68712 | 6905320 | 719732580 | 77088277288 | 16674400 |  |  |  | 145 | 138 | 130 | 123 | 114 | 102 | 90 | 75
4 | 97 | 300 | 9409 | 912673 | 88529281 | 8587340257 | 832972004929 | 29100 | 2822700 | 273801900 | 4 |  |  |  |  | 6905320 | 719732580 | 77088277288 | 8429214586092 | 1406611600
5 | 88 | 400 | 7744 | 681472 | 59969536 | 5277319168 | 464404086784 | 35200 | 3097600 | 272588800 | 5 | [12 empty] | 122 | 114 | 105 | 97 | 88 | 77 | 65 | 50
6 | 77 | 500 | 5929 | 456533 | 35153041 | 2706784157 | 208422380089 | 38500 | 2964500 | 228266500 | 6 |  |  |  |  | 1 | 89.75 | 8589 | 863165 | 350
7 | 65 | 600 | 4225 | 274625 | 17850625 | 1160290625 | 75418890625 | 39000 | 2535000 | 164775000 | 7 | X | Y |  |  | 0 | 4271.5 | 738418 | 99980110 | -42100
8 | 50 | 700 | 2500 | 125000 | 6250000 | 312500000 | 15625000000 | 35000 | 1750000 | 87500000 | 8 | 122 | 0 | n= | 8 | 0 | 738418 | 129565212 | 17778483808 | -7374800 |  | 305.9742 | 305.9742 | 122 | 114 | 105 | 97 | 88 | 77 | 65 | 50
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 98.6566 | sum(x) | 718 | 0 | 99980110 | 17778483808 | 2468784048292 | -1010250400 |  | 392.5457 | 491.2024
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 206.5744 | sum(x^2) | 68712 | [6 empty] | 478.9355 | 685.5099
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 297.9963 | sum(x^3) | 6905320 | [6 empty] | 546.9654 | 844.9617
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 394.566 | sum(x^4) | 719732580 | 1 | 0 | -6926.1622 | -1237552.5167 | 1234.578 |  | 614.836 | 1009.402
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 501.6895 | sum(x^5) | 77088277288 | 0 | 1 | 172.8709 | 23406.3233 | -9.856 |  | 687.1795 | 1188.869
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 602.1789 | sum(x^6) | 8429214586092 | 0 | 0 | 1914236.295 | 494833365.3031 | -96935.5964 |  | 755.4383 | 1357.6172
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 699.0778 | sum(y) | 2800 | 0 | 0 | 494833365.3031 | 128617269499.5151 | -24844188.833 |  | 829.7328 | 1528.8106
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0744 | 730.7635 | sum(xy) | 209200
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1949 | 731.3151 | sum(x^2y) | 16674400 | 1 | 0 | 0 | 552872.3007 | 883.842
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3639 | 732.0824 | sum(x^3y) | 1406611600 | 0 | 1 | 0 | -21281.0978 | -1.102
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5349 | 732.8519 |  |  | 0 | 0 | 1 | 258.5017 | -0.050639
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7386 | 733.7587 |  |  | 0 | 0 | 0 | 701995894.3212 | 213829.0865
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9136 | 734.5292
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9417 | 734.652 |  |  | ^b1 | ^b2 | ^b3 | ^b4 | ^Results
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 0 | 0 | 0 | 715.4362
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1 | 0 | 0 | 5.3803 | X
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1 | 0 | -0.12938 | X^2
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 1 | 0.0003046 | X^3
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0