## #3BLR70329(석공)
"붙임"
INPUT DATA SHEETS for
BOILER EFFICIENCY by HEAT LOSS METHOD
(ASME PTC 4.1)
TEST UNIT & LOAD |  |  | #3 BLR 73%(145T/H) |  | #1 BLR 100%(225T/H)
DATE |  |  | 2007. 03. 29 |  | 2006. 11. 1.
TIME |  |  | 09:30~11:30 |  | 09:30~11:30
FUEL |  |  | 중국 Shenhua Coal |  | 중국 Shenhua Coal
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
1. FUEL ANALYSIS
A. TOTAL MOISTURE (AS FIRED BASE) | mfc | % | 13.14 |  | 13.1
B. PROXIMATE ANALYSIS (AIR DRY BASIS) |  | SUM : | 100 |  | 100
1) INHERENT MOISTURE | m | % | 2.29 |  | 4.82
2) FIXED CARBON | FC | % | 53.86 |  | 53.94
3) VOLATILE MATTER | VM | % | 33.46 |  | 34.03
4) ASH | a | % | 10.39 |  | 7.21
C. ULTIMATE ANALYSIS (DRY BASIS) |  | SUM : | 100 |  | 100
1) CARBON | C' | % | 74.9 |  | 77.3
2) HYDROGEN | H' | % | 4.32 |  | 4.47
3) NITROGEN | N' | % | 1.01 |  | 1
4) SULPHUR | S' | % | 0.11 |  | 0.14
5) ASH | a' | % | 10.63 |  | 7.58
6) OXYGEN | O' | % | 9.03 |  | 9.51
7) H.H.V (AIR DRY BASE) | Hf | Kcal/kg | 6770 | * | 6790
2. FUEL CONSUMPTION | Wfe | kg/hr | 24350 |  | 24100
3. UNBURNED CARBON ANALYSIS
A. REFUSE DISTRIBUTION RATE |  | SUM : | 100 |  | 100
1) ASH PIT | Rp | % | 10 |  | 10
2) ECO. HOPPER | Re | % | 0 |  | 0
3) AH HOPPER | Ra | % | 0 |  | 0
4) EP HOPPER | Rd | % | 90 |  | 90
B. UNBURNED CARBON RATE
1) ASH PIT | Up | % | 25.57 |  | 5.09
2) ECO. HOPPER | Ue | % | 3.67 |  | 0
3) AH HOPPER | Ua | % | 3.67 |  | 0
4) EP HOPPER | Ud | % | 3.67 |  | 5.09
15-1
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
4. AIR TEMPERATURE
1) AMBIENT AIR | tA | ℃ | 21.5556 |  | 15
2) FDF OUT AIR | tA6 | ℃ | 45.4667 |  | 39.56
3) GAH OUT AIR | tA9 | ℃ | 343.6444 |  | 349.44
4) REFERENCE AIR | tRA | ℃ | 45.4667 | * | 39.56
5) REFERENCE AIR (DESIGN) | tRAD | ℃ | 32 |  | 32
6) AH INLET AIR (DESIGN) | tA8D | ℃ | 32 |  | 32
7) AH INLET PRIMARY AIR (A) | tA8pa-A | ℃ | 45.4667 | * | 39.56
8) AH INLET PRIMARY AIR (B) | tA8pa-B | ℃ | 45.4667 |  | 39.56
9) AH INLET SECONDARY AIR (A) | tA8sa-A | ℃ | 45.4667 | * | 39.56
10) AH INLET SECONDARY AIR (B) | tA8sa-B | ℃ | 45.4667 |  | 39.56
11) PRIMARY AIR WEIGHT AT | Wpa | % | 0 |  | 0
AH INLET (DESIGN) |  |  | 0 |  | 0
12) SECONDARY AIR WEIGHT AT | Wsa | % | 100 |  | 100
AH INLET (DESIGN)
5. GAS TEMPERATURE
1) A/H INLET GAS (A) | tG14-A | ℃ | 381.7444 |  | 384.67
2) A/H INLET GAS (B) | tG14-B |  | 381.7444 |  | 384.67
3) A/H OUTLET GAS (A) | tG15-A | ℃ | 154.2593 |  | 148.67
4) A/H OUTLET GAS (B) | tG15-B | ℃ | 154.2593 |  | 148.67
6. AMBIENT CONDITION
1) DRY BULB TEMP. | tA | ℃ | 21.5556 |  | 15
2) WET BULB TEMP. | tW | ℃ | 15.8889 |  | 11.5
3) RELATIVE HUMIDITY | Ø | % | 54.2222 |  | 66.5
4) ATMOS. PRESS | PA | mmHg | 760 |  | 760
5) SAT. PRESS AT tA | Ps | mmHg | 11.39 | * | 23.61
7. O2 VOL % ,DRY
1) A/H INLET GAS O2(A) | O2-A | % | 3.15 |  | 3
2) A/H INLET GAS O2(B) | O2-B | % | 3.15 |  | 3
3) A/H OUTLET GAS O2(A) | O2'-A | % | 4.4 |  | 4.2
4) A/H OUTLET GAS O2(B) | O2'-B | % | 4.4 |  | 4.2
15-2
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
8. HEAT LOSS CALCULATION DATA
1) ATMOS. PRESS. | PA | ata | 1.0332 |  | 1.0332
## 2) PARTIAL PRESS. OF VAPOR | PmG | ata | 0.08 |  | 0.093
IN FLUE GAS (FEED BACK)
3) A/H OUTLET GAS TEMP (AVE) | tG15 | ℃ | 154.2593 |  | 148.67
## 4) STM ENTHALPY AT tG15 & PmG | h15 | Kcal/kg | 652.25 |  | 664.45
5) SAT.STM ENTHALPY AT tRA | hRv | Kcal/kg | 614.47 | 45.4667 | 618.57
6) SAT.WTR ENTHALPY AT tRA | hRw | Kcal/kg | 39.039 | 45.4667 | 48.65
7) SPEC HEAT @tG15 & tRA | CPG' | Kcal/kg | 0.239 |  | 0.239
8) DESIGN RADIATION LOSS | Lβ' | % | 0.42 |  | 0.36
9) DESIGN UNMEASURED LOSS | Lum' | % | 0.5 |  | 0.5
9. HEAT CREDIT CALCULATION DATA
1) SPEC. HEAT OF AIR | cpA' | Kcal/kg℃ | 0.24 |  | 0.24
2) SPEC. HEAT OF OIL | cpO | Kcal/kg℃ | - |  | -
3) SPEC. HEAT OF COAL | cpC | Kcal/kg℃ | - |  | -
4) SPEC. HEAT OF STEAM | cpS | Kcal/kg℃ | 0.45 |  | 0.45
5) ATOM. STM ENTHALPY | hz. | Kcal/kg℃ | - |  | -
6) AUX. DRIVE POWER | kwh | KW | 485.22 |  | 485.22
CONSUMPTION
7) DRIVE EFFICIENCY | ηx | - | 0.9 |  | 0.9
10. HEAT LOSS CORRECTION DATA
1) HHV COAL (AFB) , DESIGN | HfcD | % | 6533 |  | 6533
2) MOIST. IN COAL , DESIGN | mfD | % | 9 |  | 9
3) H2 IN COAL , DESIGN | HD | % | 4.4 |  | 4.4
4) MOIST. IN AIR , DESIGN | WmA'D | kg/kg AIR | 0.014 |  | 0.014
## 5) CORRECTED GAS TEMP. | tG15δ | ℃ | 145.15 |  | 143.5
@ A/H OUTLET(FEED BACK)
## 6) STM ENTHALPY AT tG15δ,PmG | h15δ | Kcal/kg | 652.25 | 과열도가 있는 | 664.45
7) SAT. STM ENTHALPY AT | hRVD | Kcal/kg | 611.44 |  | 611.44
DESIGN REF. AIR TEMP.
8) SAT. WATER ENTHALPY | hRwD | Kcal/kg | 32.01 |  | 32.01
AT DESIGN REF. TEMP.
9) SPEC HEAT OF GAS(WET BASE) | CPG | Kcal/kg℃ | 0.246 |  | 0.246
10) FW.IN TEMP @ ECO.IN,DESIGN | FwTD | ℃ | 170 | ## | 255
11) FW.IN TEMP @ ECO.IN | FwT | ℃ | 247.4889 | ## | 250.33
11. DESIGN BLR EFFICIENCY | ηD | % | 88.38 |  | 88.38
15-3
BOILER EFFICIENCY CALCULATION
by HEAT LOSS METHOD
I. FUEL ANALYSIS
TEST UNIT & LOAD |  |  | #3 BLR 73%(145T/H) |  | #1 BLR 100%(225T/H)
DATE |  |  | 2007. 03. 29 |  | 2006. 11. 1.
TIME |  |  | 09:30~11:30 |  | 09:30~11:30
FUEL |  |  | 중국 Shenhua Coal |  | 중국 Shenhua Coal
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
1. COAL ANALYSIS
A. TOTAL MOISTURE (AS FIRED) | mfc | % | 13.14 |  | 13.1
B. PROXIMATE ANALYSIS (AIR DRY BASIS) |  | SUM : | 100 |  | 100
1) INHERENT MOISTURE | Im | % | 2.29 |  | 4.82
2) FIXED CARBON | FC | % | 53.86 |  | 53.94
3) VOLATILE MATTER | VM | % | 33.46 |  | 34.03
4) ASH | a | % | 10.39 |  | 7.21
C. ULTIMATE ANALYSIS (DRY BASIS) |  | SUM : | 100 |  | 100
1) CARBON | C' | % | 74.9 |  | 77.3
2) HYDROGEN | H' | % | 4.32 |  | 4.47
3) OXYGEN | O' | % | 9.03 |  | 9.51
4) NITROGEN | N' | % | 1.01 |  | 1
5) SULPHUR | S' | % | 0.11 |  | 0.14
6) ASH | a' | % | 10.63 |  | 7.58
7) TOTAL |  | % | 100 |  | 100
D. ULTIMATE ANALYSIS (AS FIRED BASIS)
1) CARBON | C | % | 65.0581 |  | 67.1737
2) HYDROGEN | H | % | 3.7524 |  | 3.8844
3) OXYGEN | O | % | 7.8435 |  | 8.2642
4) NITROGEN | N | % | 0.87729 |  | 0.869
5) SULPHUR | S | % | 0.095546 |  | 0.12166
6) ASH | am | % | 9.2332 |  | 6.587
7) MOISTURE | mfc | % | 13.14 |  | 13.1
8) TOTAL |  | % | 100 |  | 100
E. HIGHER HEATING VALUE
1) H.H.V (AIR DRY BASIS) | Hf | Kcal/kg | 6770 |  | 6790
2) SURFACE MOISTURE | Sm | % | 11.1 |  | 8.7
3) H.H.V (AS FIRED BASIS) | Hfc | Kcal/kg | Hfc = Hf*(100-Sm)/100 |  | Hfc = Hf*(100-Sm)/100
|  |  | 6018.5 |  | 6199.3
2. COAL CONSUMPTION | Wfe | kg/hr | 24350 |  | 24100
15-4
Ⅱ. REFUSE ANALYSIS
LOAD |  |  | #3 BLR 73%(145T/H) |  | #1 BLR 100%(225T/H)
DATE |  |  | 2007. 03. 29 |  | 2006. 11. 1.
TIME |  |  | 09:30~11:30 |  | 09:30~11:30
FUEL |  |  | 중국 Shenhua Coal |  | 중국 Shenhua Coal
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
1. UNBURNED CARBON ANALYSIS
A. REFUSE DISTRIBUTION RATE
1) ASH PIT | Rp | % | 10 |  | 10
2) ECO. HOPPER | Re | % | 0 |  | 0
3) AH HOPPER | Ra | % | 0 |  | 0
4) EP HOPPER | Rd | % | 90 |  | 90
B. UNBURNED CARBON RATE
1) ASH PIT | Up | % | 25.57 |  | 5.09
2) ECO. HOPPER | Ue | % | 3.67 |  | 0
3) AH HOPPER | Ua | % | 3.67 |  | 0
4) EP HOPPER | Ud | % | 3.67 |  | 5.09
C. UNBURNED CARBON RATE/ | U | % | U = 1/100(RpUp+ReUe+RaUa+RdUd) |  | U = 1/100(RpUp+ReUe+RaUa+RdUd)
DRY REFUSE |  |  | 5.86 |  | 5.09
D. ASH CONTENT | am | % | 9.2332 |  | 6.587
E. TOTAL DRY REFUSE / | Wd'p' | kg/kg.F | Wd'p' = am/(100-U) |  | Wd'p' = am/(100-U)
AS FIRED FUEL |  |  | 0.0981 |  | 0.0694
2. UNBURNED CARBON / | Cu | kg/kg.F | Cu = Wd'p'*U/100 |  | Cu = Wd'p'*U/100
AS FIRED FUEL |  |  | 0.0057 |  | 0.0035
3. BURNED CARBON / | Cb | kg/kg.F | Cb = C/100-Cu |  | Cb = C/100-Cu
AS FIRED FUEL |  |  | 0.6449 |  | 0.6682
15-5
Ⅲ. BOILER EFFICIENCY CALCULATION
TEST UNIT & LOAD |  |  | #3 BLR 73%(145T/H) |  | #1 BLR 100%(225T/H)
DATE |  |  | 2007. 03. 29 |  | 2006. 11. 1.
TIME |  |  | 09:30~11:30 |  | 09:30~11:30
FUEL |  |  | 중국 Shenhua Coal |  | 중국 Shenhua Coal
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
1. AIR TEMPERATURE
1) AMBIENT AIR | tA | ℃ | 21.5556 |  | 15
2) FDF OUT AIR | tA6 | ℃ | 45.4667 |  | 39.56
3) GAH OUT AIR | tA9 | ℃ | 343.6444 |  | 349.44
4) REFERENCE AIR | tRA | ℃ | 45.4667 |  | 39.56
5) REFERENCE AIR (DESIGN) | tRAD | ℃ | 32 |  | 32
6) A/H INLET AIR (DESIGN) | tA8D | ℃ | 32 |  | 32
7) A/H INLET PRIMARNY AIR (A) | tA8pa-A | ℃ | 45.4667 |  | 39.56
8) A/H INLET PRIMARNY AIR (B) | tA8pa-B | ℃ | 45.4667 |  | 39.56
9) A/H INLET PRIMARNY AIR (AVE) | tA8pa | ℃ | 45.4667 |  | 39.56
10) A/H INLET SECONDARY AIR (A) | tA8sa-A | ℃ | 45.4667 |  | 39.56
11) A/H INLET SECONDARY AIR (B) | tA8sa-B | ℃ | 45.4667 |  | 39.56
12) A/H INLET SECONDARY AIR(AVE) | tA8sa | ℃ | 45.4667 |  | 39.56
13) PRIMARY AIR WEIGHT AT | Wpa | % | 0 |  | 0
A/H INLET
14) SECONDARY AIR WEIGHT AT | Wsa | % | 100 |  | 100
A/H INLET
15) WEIGHTED AVERAGE | tA8 | tA8 = (Wpa*tA8pa+Wsa*tA8sa)/(Wpa+Wsa)
AH INLET AIR |  | ℃ | 45.4667 |  | 39.56
2. GAS TEMPERATURE
1) A/H IN GAS (A) | tG14-A | ℃ | 381.7444 |  | 384.67
2) A/H IN GAS (B) | tG14-B | ℃ | 381.7444 |  | 384.67
3) A/H IN GAS (AVE) | tG14 | ℃ | 381.7444 |  | 384.67
4) A/H OUT GAS (A) | tG15-A | ℃ | 154.2593 |  | 148.67
5) A/H OUT GAS (B) | tG15-B | ℃ | 154.2593 |  | 148.67
6) A/H OUT GAS (AVE) | tG15 | ℃ | 154.2593 |  | 148.67
15-6
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
3. MOISTURE IN AIR
1) DRY BULB TEMP. | tA | ℃ | 21.5556 |  | 15
2) WET BULB TEMP. | tW | ℃ | 15.8889 |  | 11.5
3) RELATIVE HUMIDITY | Ø | % | 54.2222 |  | 66.5
4) ATMOS. PRESS | PA | mmHg | 760 |  | 760
5) SAT. PRESS AT tA | Ps | mmHg | 11.39 |  | 23.61
6) PARTIAL PRESS OF VAPOR | PmA | mmHg | PmA = Ø*Ps/100 |  | PmA = Ø*Ps/100
IN WET AIR |  |  | 6.18 |  | 15.7
7) MOIST IN DRY AIR | WmA' | kg/kgAIR | WmA' = 0.622*PmA/(PA-PmA) |  | WmA' = 0.622*PmA/(PA-PmA)
|  |  | 0.0051 |  | 0.0131
4. A/H INLET GAS ANALYSIS
1) O2(A) | O2-A | % | 3.15 |  | 3
2) O2(B) | O2-B | % | 3.15 |  | 3
3) O2(AVE) | O2 | % | 3.15 |  | 3
4) CO2(A) | CO2-A | % | 16.6 | ## | 17.5
5) CO2(B) | CO2-B | % | 16.6 |  | 17.5
6) CO2(AVE) | CO2 | % | 16.6 |  | 17.5
7) N2 | N2 | % | N2 = 100 - (O2 + CO2) |  | N2 = 100 - (O2 + CO2)
|  |  | 80.25 |  | 79.5
5. A/H OUT GAS ANALYSIS
1) O2(A) | O2'-A | % | 4.4 |  | 4.2
2) O2(B) | O2'-B | % | 4.4 |  | 4.2
3) O2(AVE) | O2' | % | 4.4 |  | 4.2
4) CO2(A) | CO2'-A | % | 15.65 | ## | 16.3
5) CO2(B) | CO2'-B | % | 15.65 |  | 16.3
6) CO2(AVE) | CO2' | % | 15.65 |  | 16.3
7) N2 | N2' | % | N2' = 100 - (O2 '+ CO2') |  | N2' = 100 - (O2 '+ CO2')
|  |  | 79.95 |  | 79.5
6. DRY GAS WEIGHT
1) A/H INLET GAS | WG'14 | WG'=[(44.01*CO2+32.0*O2+28.02*N2
+28.01*CO)/(12.01*(CO2+CO))]
*[Cb+(12.01*S/100)/32.07]
|  | kg/kg.F | 9.968 |  | 9.843
2) A/H OUTLET GAS | WG'15 | kg/kg.F | 10.539 |  | 10.518
15-7
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
7. N2 WEIGHT
1) A/H INLET GAS | WG'14N2 | kg/kg.F | WG'N2=28.02*N2/(12.01*(CO2+CO)) |  | WG'N2=28.02*N2/(12.01*(CO2+CO))
|  |  | *(Cb+12.01*S/(100*32.07) |  | *(Cb+12.01*S/(100*32.07)
|  |  | 7.278 |  | 7.087
2) A/H OUTLET GAS | WG'15N2 | kg/kg.F | 7.691 |  | 7.609
8. DRY AIR WEIGHT
1) A/H OUTLET GAS | WA'9 | kg/kg.F | WA' = (WG'N2-N/100)/0.7685 |  | WA' = (WG'N2-N/100)/0.7685
|  |  | 9.459 |  | 9.211
2) A/H INLET GAS | WA'8 | kg/kg.F | 9.996 |  | 9.89
9. MOSIT. IN AH INLET GAS | WmG14 | WmG14 = 8.936*H/100+WmA'*WA'9+mf/100
|  | kg/kg.F | 0.515 |  | 0.599
10. MOSIT. IN AH OUTLET GAS | WmG15 | WmG15 = WmG14+(WG'15-WG'14)*WmA'
|  | kg/kg.F | 0.518 |  | 0.608
11. AH LEAKAGE RATIO | AL | AL = [(WG'15+WmG15)-(WG'14+WmG14)]/
(WG'14+WmG14)*100
|  | % | 5.476 |  | 6.55
12. EXCESS AIR
1) THEORETICAL AIR | Aθ | Aθ=[11.51*Cb+[34.30*(H-O/7.937)
+4.335*S]/100
|  | kg/kg.F | 8.375 |  | 8.671
2) EXCESS AIR | Ax | % | Ax = [(WA'9-Aθ)/Aθ]*100 |  | Ax = [(WA'9-Aθ)/Aθ]*100
(ECO. OUT BASE) |  |  | 12.94 |  | 6.23
13. HEAT LOSS CALCULATION
1) ATMOS. PRESS. | PA | ata | 1.0332 |  | 1.0332
2) PARTIAL PRESS. OF VAPOR | PmG | PmG = PA/[1+(100*1.5*Cb)/(WmG15
IN FLUE GAS |  | *(CO2+CO))]
|  | ata | 0.08 |  | 0.093
3) STM ENTHALPY AT tG15 & PmG | h15 | Kcal/kg | 652.25 | ## | 664.45
4) SAT.STM ENTHALPY AT tRA | hRv | Kcal/kg | 614.47 |  | 618.57
5) SAT.WTR ENTHALPY AT tRA | hRw | Kcal/kg | 39.039 |  | 48.65
6) SPEC HEAT @tG15 & tRA | CPG' | Kcal/kg | 0.239 |  | 0.239
7) DESIGN RADIATION LOSS | Lβ' | % | 0.42 |  | 0.36
8) DESIGN UNMEASURED LOSS | Lum' | % | 0.5 |  | 0.5
15-8
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
14. HEAT LOSSES
1) DRY GAS LOSS | LG' | Kcal/kg | LG' = WG'15*CPG'*(tG15-tRA) |  | LG' = WG'15*CPG'*(tG15-tRA)
|  |  | 274.03 | ## | 274.28
2) MOIST IN FUEL LOSS | Lmf | Kcal/kg | Lmf = (mfc/100)*(h15-hRw) |  | Lmf = (mfc/100)*(h15-hRw)
|  |  | 80.58 |  | 80.67
3) MOISTURE FROM BURNING | LH | Kcal/kg | LH = 8.936*(H/100)*(h15-hRw) |  | LH = 8.936*(H/100)*(h15-hRw)
OF HYDROGEN LOSS |  |  | 205.62 |  | 213.75
4) ATOMIZING STEAM LOSS | Lz | Kcal/kg | Lz = (Wze/Wfe)*(h15-hRv) |  | Lz = (Wze/Wfe)*(h15-hRv)
|  |  | 0 |  | 0
5) MOIST IN AIR LOSS | LmA | Kcal/kg | LmA = WmA'*WA'8*(h15-hRv) |  | LmA = WmA'*WA'8*(h15-hRv)
|  |  | 1.93 |  | 5.94
6) RADIATION LOSS | Lβ | Lβ= DESIGN RAD. LOSS(Lβ')*Hfc/100
|  | Kcal/kg | 25.28 |  | 22.32
7) UNBURNED CARBON LOSS | Luc | Kcal/kg | Luc = 8100*Cu |  | Luc = 8100*Cu
|  |  | 46.17 | ## | 28.35
8) UNMEASURED LOSS | Lum | Kcal/kg | Lum = DESIGN Lum'(%)*Hfc/100 |  | Lum = DESIGN Lum'(%)*Hfc/100
|  |  | 30.09 |  | 31
9) TOTAL LOSS | L | L = LG'+Lmf+LH+Lz+LmA+Lβ+Luc+Lum
|  | Kcal/kg | 663.7 |  | 656.31
15. HHV OF FUEL | Hfc | Kcal/kg | 6018.5 |  | 6199.3
16. HEAT CREDIT CALCULATION DATA
1) SPEC. HEAT OF AIR | cpA' | Kcal/kg℃ | 0.24 |  | 0.24
2) SPEC. HEAT OF OIL | cpO | Kcal/kg℃ | - |  | -
3) SPEC. HEAT OF COAL | cpC | Kcal/kg℃ | - |  | -
4) SPEC. HEAT OF STEAM | cpS | Kcal/kg℃ | 0.45 |  | 0.45
5) ATOM. STM ENTHALPY | hz. | Kcal/kg℃ | - |  | -
6) AUX. DRIVER POWER | kwh | KW | 485.22 |  | 485.22
CONSUMPTION
7) DRIVER EFFICIENCY | ηx | - | 0.9 |  | 0.9
15-9
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
17. HEAT CREDITS
1) HEAT IN ENTERING AIR | BA | Kcal/kg.F | BA = WA'8*cpA'*(tA8-tRA) |  | BA = WA'8*cpA'*(tA8-tRA)
|  |  | 0 |  | 0
2) HEAT IN ATOMIZING STEAM | Bz | Kcal/kg.F | Bz = x*(hz-hRv) |  | Bz = x*(hz-hRv)
|  |  | 0 |  | 0
3) SENSIBLE HEAT IN FUEL | Bf | Kcal/kg.F | Bf = cpO*(tfo-tRA) |  | Bf = cpO*(tfo-tRA)
|  |  | 0 |  | 0
4) HEAT SUPPLIED BY | Bx | Kcal/kg.F | Bx = (860*kWh*ηx)/Wfe |  | Bx = (860*kWh*ηx)/Wfe
AUX. DRIVERS |  |  | 15.42 |  | 15.58
5) HEAT SUPPLIED BY | BmA | Kcal/kg.F | BmA = WmA'*WA'8*cpS*(tA8-tRA) |  | BmA = WmA'*WA'8*cpS*(tA8-tRA)
MOISTURE IN AIR |  |  | 0 |  | 0
6) TOTAL | B | Kcal/kg.F | 15.42 |  | 15.58
18. HEAT LOSS PERCENTAGE
1) DRY GAS LOSS | LG'(%) | % | LG'(%) = LG'*100/(Hfc+B) |  | LG'(%) = LG'*100/(Hfc+B)
|  |  | 4.5415 |  | 4.4133
2) MOISTURE IN FUEL LOSS | Lmf(%) | % | Lmf(%) = LmF*100/(Hfc+B) |  | Lmf(%) = LmF*100/(Hfc+B)
|  |  | 1.34 |  | 1.3
3) MOISTURE FROM BURNING | LH(%) | % | LH(%) = LH*100/(Hfc+B) |  | LH(%) = LH*100/(Hfc+B)
OF HYDROGEN LOSS |  |  | 3.42 |  | 3.45
4) MOIST. IN AIR LOSS | LmA(%) | % | LmA(%) = LmA*100/(Hfc+B) |  | LmA(%) = LmA*100/(Hfc+B)
|  |  | 0.03 |  | 0.1
5) RADIATION LOSS | Lβ(%) | % | Lβ(%) = Lβ*100/(Hfc+B) |  | Lβ(%) = Lβ*100/(Hfc+B)
|  |  | 0.42 |  | 0.36
6) UNBURNED CARBON LOSS | Luc(%) | % | Luc(%) = Luc*100/(Hfc+B) |  | Luc(%) = Luc*100/(Hfc+B)
|  |  | 0.77 |  | 0.46
7) UNMEASURED LOSS | Lum(%) | % | Lum(%) = Lum*100/(Hfc+B) |  | Lum(%) = Lum*100/(Hfc+B)
|  |  | 0.5 |  | 0.5
8) TOTAL LOSS | L(%) | % | 11.0215 |  | 10.5833
19. MEASURED BOILER EFFICIENCY | ηm | % | ηm = 100-L(%) |  | ηm = 100-L(%)
|  |  | 88.98 |  | 89.42
20. DESIGN BLR EFFICIENCY | ηD | % | 88.38 |  | 88.38
21. EFFICIENCY DEVIATION | Δη | % | ηm = ηm-ηD |  | ηm = ηm-ηD
|  |  | 0.6 |  | 1.04
15-10
EFFICIENCY CORRECTION for
GUARANTEE CONDITION |  |  |  | 0
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
22. HEAT CREDIT CORRECTION (FOR REFERENCE AIR TEMP.)
1) HEAT IN ENTERING AIR | ΔBA | Kcal/kg.F | ΔBA = WA'8*CPA'(tRAD-tRA) |  | ΔBA = WA'8*CPA'(tRAD-tRA)
|  |  | -32.31 |  | -17.94
2) HEAT IN ATOMIZING STEAM | ΔBz | Kcal/kg.F | ΔBz = (Wze/wfe)*(tRAD-tRA) |  | ΔBz = (Wze/wfe)*(tRAD-tRA)
|  |  | 0 |  | 0
3) SENSIBLE HEAT IN FUEL | ΔBf | Kcal/kg.F | ΔBf = CPO*(tRAD-tRA) |  | ΔBf = CPO*(tRAD-tRA)
|  |  | 0 |  | 0
4) HEAT SUPPLIED BY | ΔBmA | Kcal/kg.F | ΔBmA=WmA'*WA'8*cpS*(tRAD-tRA) |  | ΔBmA=WmA'*WA'8*cpS*(tRAD-tRA)
MOIST IN AIR |  |  | -0.31 |  | -0.44
5) TOTAL | ΔB | Kcal/kg.F | -32.62 |  | -18.38
23. HEAT LOSS CORRECTION DATA
1) C/H RATIO | C/H | - | C/H=Carbon WT%/Hydrogen WT% |  | C/H=Carbon WT%/Hydrogen WT%
|  |  | 17.34 |  | 17.29
2) MOIST. IN FUEL , DESIGN | mfD | % | 9 |  | 9
3) H2 IN FUEL , DESIGN | HD | % | 4.4 |  | 4.4
4) MOIST. IN AIR , DESIGN | WmA'D | kg/kg AIR | 0.014 |  | 0.014
5) CORRECTED GAS TEMP. | tG15δ | ℃ | tG15δ=[tA8D*(tG14-tG15)+tG14* |  | tG15δ=[tA8D*(tG14-tG15)+tG14*
(A/H OUTLET) |  |  | (tG15-tA8)]/(tG14-tA8) |  | (tG15-tA8)]/(tG14-tA8)
|  |  | 145.15 |  | 143.5
6) STM ENTHALPY AT tG15δ,PmG | h15δ | Kcal/kg | 652.25 |  | 664.45
7) SAT. STM ENTHALPY AT | hRVD | Kcal/kg | 611.44 |  | 611.44
DESIGN REF. AIR TEMP.
8) SAT. WATER ENTHALPY | hRwD | Kcal/kg | 32.01 |  | 32.01
AT DESIGN REF. TEMP.
9) SPEC HEAT OF GAS(WET BASE) | CPG | Kcal/kg℃ | 0.246 |  | 0.246
15-11
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
24. HEAT LOSS CORRECTION
A. FOR REFERENCE AIR TEMP.
1) DRY GAS LOSS CORRECTION | ΔLG' | Kcal/kg.F | ΔLG'=WG'15*CPG'*[(tG15δ-tRAD) |  | ΔLG'=WG'15*CPG'*[(tG15δ-tRAD)
|  |  | -(tG15-tRA)] |  | -(tG15-tRA)]
|  |  | 10.98 |  | 6.01
2) MOISTURE IN FUEL LOSS | ΔLmf1 | Kcal/kg.F | ΔLmF1=(mfc/100)*[(h15δ-hRwD) |  | ΔLmF1=(mfc/100)*[(h15δ-hRwD)
CORRECTION |  |  | -(h15-hRw) |  | -(h15-hRw)
|  |  | 0.92 |  | 2.18
3) MOISTURE FROM BURNING OF | ΔLH1 | ΔLmF1=8.936*(H/100)*[(h15δ-hRwD)
HYDROGEN LOSS CORRECTION |  | -(h15-hRw)]
|  | Kcal/kg.F | 2.36 |  | 5.78
4) MOISTURE IN AIR LOSS | ΔLmA1 | Kcal/kg.F | ΔLmA1=WmA'*WA'8*[(h15δ-hRwD) |  | ΔLmA1=WmA'*WA'8*[(h15δ-hRwD)
CORRECTION |  |  | -(h15-hRw)] |  | -(h15-hRw)]
|  |  | 0.15 |  | 0.92
5) ATOMIZING STEAM LOSS | ΔLz | Kcal/kg.F | ΔLz=x*[(h15δ-hRwD)-(h15-hRv)] |  | ΔLz=x*[(h15δ-hRwD)-(h15-hRv)]
CORRECTION |  |  | 0 |  | 0
B. FOR H2 IN FUEL
1) MOISTURE IN FUEL LOSS | ΔLmf2 | ΔLmf2 = [(mfD-mfc)/100]*(h15δ-hRwD)
CORRECTION |  | Kcal/kg | -25.68 |  | -25.93
2) MOISTURE FROM BURNING | ΔLH2 | ΔLH2 = [8.936(HD-H)/100]*(h15δ-hRwD)
OF HYDROGEN CORRECTION |  | Kcal/kg | 35.9 |  | 29.14
C. FOR MOISTURE IN AIR
1) MOISTURE IN AIR LOSS | ΔLmA2 | ΔLmA2 = (WmA'D-WmA')*WA'8*(h15δ-hRwD)
CORRECTION |  | Kcal/kg | 3.63 |  | 0.47
D. GROSS CALORIFIC VALUE | ΔLHHV | % | 0 | ΔLHHV(%)= (Hfc- | 0.42
CORRECTION |  |  |  | HfcD)*(-0.5/400)
←KUMI #1 80%
E. ECO.INLET FEED WATER TEMP. | ΔLFw | % | 0.23 | ΔLFw(%)= (FwT- | -0.01
CORRECTION |  |  |  | FwTD)*(0.12/40)
←KUMI #1 80%
F. TOTAL CORRECTION | ΔL | Kcal/kg | 28.26 |  | 18.57
25. CORRECTED BOILER EFFICIENCY | ηc | ηc=[1-(L+ΔL)/(Hfm+B-ΔB)]+ΔLHHV+ ΔLFw
0 |  | % | 88.82 |  | 89.58
*. EFFICIENCY CORRECTION | Δηc | % | -0.16 | Δηc = ηc-ηm | 0.16
26. DESIGN BLR EFFICIENCY | ηD | % | 88.38 |  | 88.38
27. EFFICIENCY DEVIATION | Δη | % | 0.44 | Δη = ηc-ηD | 1.2
15-12
IV. CO2 CALCULATION (VOL % , DRY)
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
1. COAL ANALYSIS (AS FIRED BASIS) |  |  |  | 0
1) CARBON | C | kg/kg.F | 0.65058 |  | 0.67174
2) HYDROGEN | H | kg/kg.F | 0.037524 |  | 0.038844
3) OXYGEN | O | kg/kg.F | 0.078435 |  | 0.082642
4) NITROGEN | N | kg/kg.F | 0.0087729 |  | 0.00869
5) SULPHUR | S | kg/kg.F | 0.00095546 |  | 0.0012166
6) ASH | am | kg/kg.F | 0.092332 |  | 0.06587
7) MOISTURE | mfc | kg/kg.F | 0.1314 |  | 0.131
8) TOTAL |  | kg/kg.F | 1 |  | 1
2. BURNED CARBON / AS FIRED FUEL | Cb | kg/kg.F | 0.6449 |  | 0.6682
3. CO2 VOL % AT THE AH INLET
1) O2 | O2 | % | 3.15 |  | 3
2) THEORETICAL DRY AIR | TDA | TDA = 11.51*Cb+34.3*(H-O/7.937)+4.335*S
|  | kg/kg.F | 8.375 |  | 8.6715
3) EXCESS AIR | Ax | Ax = 100*{(O2/100)*(31.32*Cb+11.528*S+
13.443*N+10.331*TDA)/[TDA*(2.73-
13.068*O2/100)]}
|  | kg/kg.F | 17.3347 |  | 16.3726
4) CO2 VOL%,DRY | CO2 | CO2' = 100*{(31.32*Cb+11.528*S)/[31.32
*Cb+11.528*S+13.443*N+TDA*(10.331+
(incl. SO2) |  | 13.068*Ax'/100)]}
|  | % | 16.0619 |  | 16.2093
4. CO2 VOL % AT THE AH OUTLET
1) O2 | O2' | % | 4.4 |  | 4.2
2) THEORETICAL DRY AIR | TDA' | TDA' = 11.51*Cb+34.3*(H-O/7.937)+4.335*S
|  | kg/kg.F | 8.3778 |  | 8.6743
3) EXCESS AIR | Ax' | Ax' = 100*{(O2/100)*(31.32*Cb+11.528*S+
13.443*N+10.331*TDA)/[TDA*(2.73-
13.068*O2/100)]}
|  | kg/kg.F | 26.0403 |  | 24.5617
4) CO2 VOL%,DRY | CO2' | CO2' = 100*{(31.32*Cb+11.528*S)/[31.32
*Cb+11.528*S+13.443*N+TDA*(10.331+
(incl. SO2) |  | 13.068*Ax'/100)]}
|  | % | 14.9312 |  | 15.1231
15-13
| 공기예열기 성능시험 결과 계산 |  |  | 0
LOAD |  |  | #3 BLR 73%(145T/H) |  | #1 BLR 100%(225T/H)
DATE |  |  | 2007. 03. 29 |  | 2006. 11. 1.
TIME |  |  | 09:30~11:30 |  | 09:30~11:30
FUEL |  |  | 중국 Shenhua Coal |  | 중국 Shenhua Coal
ITEM | SYMBOL | UNIT | RESULT | 비 고 | RESULT
1. GAS SIDE EFFICIENCY
1) GAH IN AIR TEMP. | tA8 | ℃ | 45.4667 |  | 39.56
2) GAH OUT AIR TEMP. | tA9 | ℃ | 343.6444 |  | 349.44
3) GAH IN GAS TEMP. | tG14 | ℃ | 381.7444 |  | 384.67
4) GAH OUT GAS TEMP(measured) | tG15 | ℃ | 154.2593 |  | 148.67
5) GAH OUT GAS TEMP. | tG15[NL] | ℃ | tG15[NL] = tG15 + (WA[L]*CPA |  | tG15[NL] = tG15 + (WA[L]*CPA
(NO - leakage) |  |  | *(tG15-tA8)/(100*CPG)) |  | *(tG15-tA8)/(100*CPG))
|  |  | 160.07 |  | 155.64
6) CORRECTED EFFICIENCY | ηG | % | ηG = (tG14-tG15[NL]*100/ |  | ηG = (tG14-tG15[NL]*100/
(tG14-tA8)
|  |  | 65.92 |  | 66.36
2. X - RATIO
1) GAH IN GAS TEMP. | tG14 | ℃ | 381.7444 |  | 384.67
2) GAH OUT GAS TEMP. | tG15[NL] | ℃ | 160.07 |  | 155.64
(NO - leakage)
3) GAH OUT AIR TEMP. | tA9 | ℃ | 343.6444 |  | 349.44
4) GAH IN AIR TEMP. | tA8 | ℃ | 45.4667 |  | 39.56
5) X - RATIO | X | X = (tG14-tG15[NL])/(tA9-tA8)
|  |  | 0.74 |  | 0.74
3. 열 회수율
1) GAH 열 회수량 | Qhr | kcal/kg.F | Qhr={WG'14*CPG'*(tG14-tG15)}+ |  | Qhr={WG'14*CPG'*(tG14-tG15)}+
|  |  | {WmG14*0.45*(tG14-tG15)}+ |  | {WmG14*0.45*(tG14-tG15)}+
|  |  | {0.2*Wd'14*(tG14-tG15)}- |  | {0.2*Wd'14*(tG14-tG15)}-
|  |  | {0.245*WA[L]*(tG15-tA8)} |  | {0.245*WA[L]*(tG15-tA8)}
|  |  | 1032.88 |  | 1065.1
2) 연료 발열량 | Hfc | kcal/kg | 6018.5 |  | 6199.3
3) GAH 열 회수율 | Rhr | % | Rhr = (Qhr*100)/Hfc |  | Rhr = (Qhr*100)/Hfc
|  |  | 17.16 |  | 17.18
15-14
ITEM | SYMBOL | UNIT | RESULT |  | RESULT
4. 과잉 공기율
1) GAH 입구 과잉공기율 | m₁ | - | m = (21*N2)/(21*N2-79*O2) |  | m = (21*N2)/(21*N2-79*O2)
|  |  | 1.173 |  | 1.165
2) GAH 출구 과잉공기율 | m₂ | - | 1.261 |  | 1.248
5. 열 관류율
1) 전열량 | Q | kcal/hr | Q = Qhr * Wfe |  | Q = Qhr * Wfe
|  |  | 25150628.0001 |  | 25668910
2) 전열면적 | A | ㎡ | 8590 |  | 8590
3) LMTD | tm | ℃ | Δtm={(tG14-tA9)-(tG15[NL] - |  | Δtm={(tG14-tA9)-(tG15[NL] -
|  |  | tA8)} / ln{(tG14-tA9) / |  | tA8)} / ln{(tG14-tA9) /
|  |  | (tG15[NL] - tA8)} |  | (tG15[NL] - tA8)}
|  |  | 69.47 |  | 67.81
4) 열 관류율 | K | kcal | K = Q / (A * tm) |  | K = Q / (A * tm)
/㎡h℃
|  |  | 42.15 |  | 44.07
6. GAH LEAKAGE
1) DRY GAS ECO. OUT | WG'14 | kg/kg.F | 9.968 |  | 9.843
2) MOIST.IN ECO.OUT GAS | WmG14 | kg/kg.F | 0.515 |  | 0.599
3) WET GAS ECO.OUT | WG14 | kg/kg.F | WG14 = WG'14 + WmG14 |  | WG14 = WG'14 + WmG14
|  |  | 10.483 |  | 10.442
4) DRY GAS GAH OUT | WG'15 | kg/kg.F | 10.539 |  | 10.518
5) MOIST.IN GAH OUT GAS | WmG15 | kg/kg.F | 0.518 |  | 0.608
6) WET GAS GAH OUT | WG15 | kg/kg.F | WG15 = WG'15 + WmG15 |  | WG15 = WG'15 + WmG15
|  |  | 11.057 |  | 11.126
7) GAH LEAKAGE RATIO | A[L] | % | A[L] = (WG15-WG14) / WG14 |  | A[L] = (WG15-WG14) / WG14
|  |  | 5.476 |  | 6.55
15-15
Note on E28: HP: 단위가 kg 이므로 TON과 혼돈하지 말것
Note on E36: HP: BOTTOM HOPPER DRAG CHAIN 30분 정지후 기동 SAMPLING
Note on E39: HP: EP HOPPER 1 FIELD LEFT,RIGHT UBC AVERAGE
Note on E44: HP: 대기온도 건습구온도계로 실측하여 평균치 적용
Note on E45: HP: CRT에 들어오는 값을 평균하여 적용
Note on E46: HP: CRT에 들어오는값을 평균하여 적용
Note on E48: HP: 불변값 : 32.00
Note on E56: HP: 불변값 : 100.0
Note on E67: HP: 불변값 : 760 mmHg
Note on E68: HP: DRY BULB TEMP (E64)에 대한 포화증기 압력 : STM TABLE에서 확인
Note on E70: HP: 환경팀 ORSAT 분석치 평균값
Note on E72: HP: 환경팀 ORSAT 분석치 평균값
Note on E87: HP: 불변값 : 1.033
Note on E92: HP: FDF OUT AIR TEMP (E45)값의 포화증기 엔탈피: STM TABLE 에서 확인
Note on E93: HP: FDF OUT AIR TEMP (E45) 값의 포화수 엔탈피 : STM TABLE 에서 확인
Note on E94: HP: 불변값 : 0.239
Note on E95: HP: 가변값 : BLR 부하별 DESIGN 값을 SPEC. 에서 찾아 적용
Note on E96: HP: 불변값 : 0.50
Note on E98: HP: 불변값 : 0.24
Note on E101: HP: 불변값 : 0.45
Note on E103: HP: 불변값 : 485.22
Note on E105: HP: 불변값 : 0.9
Note on E107: HP: 불변값 : 6,533.0 (성능탄)
Note on E108: HP: 불변값 : 9.0
Note on E109: HP: 불변값 : 4.40
Note on E110: HP: 불변값 : 0.014
Note on E114: HP: 불변값 : 32℃ 포화증기 엔탈피
Note on E116: HP: 불변값 : 32℃ 포화수 엔탈피
Note on E118: HP: 불변값 : 0.246
Note on E119: HP: 불변값 : 170.0 #3BLR F/W DESIGN TEMP
Note on E121: HP: BLR LOAD별 DESIGN 값을 적용
Note on E407: HP: DESIGN 방열율에 의해 계산된 방열량의 총 입열량에 대한 비 (고위발열량+부가열중)
Note on E415: HP: BLR LOAD별 DESIGN값을 계산하여 적용
Note on F113: HP:

## #2BLR70609
"붙임"
INPUT DATA SHEETS for
BOILER EFFICIENCY by HEAT LOSS METHOD
(ASME PTC 4.1)
TEST UNIT & LOAD |  |  | #2 BLR 100%(225T/H)
DATE |  |  | 2007. 6. 09.(O/H전 성능시험)
TIME |  |  | 09:30~11:30
FUEL |  |  | 중국 Shenhua Coal
ITEM | SYMBOL | UNIT | RESULT | 비 고
1. FUEL ANALYSIS
A. TOTAL MOISTURE (AS FIRED BASE) | mfc | % | 13.04 | 2007.06.10분석치
B. PROXIMATE ANALYSIS (AIR DRY BASIS) |  | SUM : | 99.9
1) INHERENT MOISTURE | m | % | 5.2 | 2007.06.10분석치
2) FIXED CARBON | FC | % | 54.6 | 2007.06.10분석치
3) VOLATILE MATTER | VM | % | 32.7 | 2007.06.10분석치
4) ASH | a | % | 7.4 | 2007.06.10분석치
C. ULTIMATE ANALYSIS (DRY BASIS) |  | SUM : | 100
1) CARBON | C' | % | 78.7 | 2007.05.21석공치
2) HYDROGEN | H' | % | 4.54 | 2007.05.21석공치
3) NITROGEN | N' | % | 0.99 | 2007.05.21석공치
4) SULPHUR | S' | % | 0.17 | 2007.05.21석공치
5) ASH | a' | % | 6.84 | 2007.05.21석공치
6) OXYGEN | O' | % | 8.76 | 2007.05.21석공치
7) H.H.V (AIR DRY BASE) | Hf | Kcal/kg | 6890 | 2007.06.10분석치
2. FUEL CONSUMPTION | Wfe | kg/hr | 24350 | 입력완료
3. UNBURNED CARBON ANALYSIS
A. REFUSE DISTRIBUTION RATE |  | SUM : | 100
1) ASH PIT | Rp | % | 10
2) ECO. HOPPER | Re | % | 0
3) AH HOPPER | Ra | % | 0
4) EP HOPPER | Rd | % | 90
B. UNBURNED CARBON RATE
1) ASH PIT | Up | % | 28.77
2) ECO. HOPPER | Ue | % | 13.84
3) AH HOPPER | Ua | % | 0
4) EP HOPPER | Ud | % | 4.69
ITEM | SYMBOL | UNIT | RESULT | 비 고
4. AIR TEMPERATURE
1) AMBIENT AIR | tA | ℃ | 21.5556
2) FDF OUT AIR | tA6 | ℃ | 45.4667
3) GAH OUT AIR | tA9 | ℃ | 343.6444
4) REFERENCE AIR | tRA | ℃ | 45.4667 | *
5) REFERENCE AIR (DESIGN) | tRAD | ℃ | 32
6) AH INLET AIR (DESIGN) | tA8D | ℃ | 32
7) AH INLET PRIMARY AIR (A) | tA8pa-A | ℃ | 45.4667 | *
8) AH INLET PRIMARY AIR (B) | tA8pa-B | ℃ | 45.4667
9) AH INLET SECONDARY AIR (A) | tA8sa-A | ℃ | 45.4667 | *
10) AH INLET SECONDARY AIR (B) | tA8sa-B | ℃ | 45.4667
11) PRIMARY AIR WEIGHT AT | Wpa | % | 0
AH INLET (DESIGN) |  |  | 0
12) SECONDARY AIR WEIGHT AT | Wsa | % | 100
AH INLET (DESIGN)
5. GAS TEMPERATURE
1) A/H INLET GAS (A) | tG14-A | ℃ | 381.7444
2) A/H INLET GAS (B) | tG14-B | ℃ | 381.7444
3) A/H OUTLET GAS (A) | tG15-A | ℃ | 154.2593
4) A/H OUTLET GAS (B) | tG15-B | ℃ | 154.2593
6. AMBIENT CONDITION
1) DRY BULB TEMP. | tA | ℃ | 21.5556
2) WET BULB TEMP. | tW | ℃ | 15.8889
3) RELATIVE HUMIDITY | Ø | % | 54.2222
4) ATMOS. PRESS | PA | mmHg | 760
5) SAT. PRESS AT tA | Ps | mmHg | 19.2 | *
7. O2 VOL % ,DRY
1) A/H INLET GAS O2(A) | O2-A | % | 3.15
2) A/H INLET GAS O2(B) | O2-B | % | 3.15
3) A/H OUTLET GAS O2(A) | O2'-A | % | 4.4
4) A/H OUTLET GAS O2(B) | O2'-B | % | 4.4
ITEM | SYMBOL | UNIT | RESULT | 비 고
8. HEAT LOSS CALCULATION DATA
1) ATMOS. PRESS. | PA | ata | 1.0332
## 2) PARTIAL PRESS. OF VAPOR | PmG | ata | 0.084
IN FLUE GAS (FEED BACK)
3) A/H OUTLET GAS TEMP (AVE) | tG15 | ℃ | 154.2593
## 4) STM ENTHALPY AT tG15 & PmG | h15 | Kcal/kg | 654.32
5) SAT.STM ENTHALPY AT tRA | hRv | Kcal/kg | 617.22 | 45.47
6) SAT.WTR ENTHALPY AT tRA | hRw | Kcal/kg | 46.484 | 45.47
7) SPEC HEAT @tG15 & tRA | CPG' | Kcal/kg | 0.239
8) DESIGN RADIATION LOSS | Lβ' | % | 0.31
9) DESIGN UNMEASURED LOSS | Lum' | % | 0.5
9. HEAT CREDIT CALCULATION DATA
1) SPEC. HEAT OF AIR | cpA' | Kcal/kg℃ | 0.24
2) SPEC. HEAT OF OIL | cpO | Kcal/kg℃ | -
3) SPEC. HEAT OF COAL | cpC | Kcal/kg℃ | -
4) SPEC. HEAT OF STEAM | cpS | Kcal/kg℃ | 0.45
5) ATOM. STM ENTHALPY | hz. | Kcal/kg℃ | -
6) AUX. DRIVE POWER | kwh | KW | 485.22
CONSUMPTION
7) DRIVE EFFICIENCY | ηx | - | 0.9
10. HEAT LOSS CORRECTION DATA
1) HHV COAL (AFB) , DESIGN | HfcD | % | 6533
2) MOIST. IN COAL , DESIGN | mfD | % | 9
3) H2 IN COAL , DESIGN | HD | % | 4.4
4) MOIST. IN AIR , DESIGN | WmA'D | kg/kg AIR | 0.014
## 5) CORRECTED GAS TEMP. | tG15δ | ℃ | 145.15
@ A/H OUTLET(FEED BACK)
## 6) STM ENTHALPY AT tG15δ,PmG | h15δ | Kcal/kg | 654.32
7) SAT. STM ENTHALPY AT | hRVD | Kcal/kg | 611.44
DESIGN REF. AIR TEMP.
8) SAT. WATER ENTHALPY | hRwD | Kcal/kg | 32.01
AT DESIGN REF. TEMP.
9) SPEC HEAT OF GAS(WET BASE) | CPG | Kcal/kg℃ | 0.246
10) FW.IN TEMP @ ECO.IN,DESIGN | FwTD | ℃ | 255 | ##
11) FW.IN TEMP @ ECO.IN | FwT | ℃ | 247.4889 | ##
11. DESIGN BLR EFFICIENCY | ηD | % | 88.38
BOILER EFFICIENCY CALCULATION
by HEAT LOSS METHOD
I. FUEL ANALYSIS
TEST UNIT & LOAD |  |  | #2 BLR 100%(225T/H)
DATE |  |  | 2007. 6. 09.(O/H전 성능시험)
TIME |  |  | 09:30~11:30
FUEL |  |  | 중국 Shenhua Coal
ITEM | SYMBOL | UNIT | RESULT | 비 고
1. COAL ANALYSIS
A. TOTAL MOISTURE (AS FIRED) | mfc | % | 13.04
B. PROXIMATE ANALYSIS (AIR DRY BASIS) |  | SUM : | 99.9
1) INHERENT MOISTURE | Im | % | 5.2
2) FIXED CARBON | FC | % | 54.6
3) VOLATILE MATTER | VM | % | 32.7
4) ASH | a | % | 7.4
C. ULTIMATE ANALYSIS (DRY BASIS) |  | SUM : | 100
1) CARBON | C' | % | 78.7
2) HYDROGEN | H' | % | 4.54
3) OXYGEN | O' | % | 8.76
4) NITROGEN | N' | % | 0.99
5) SULPHUR | S' | % | 0.17
6) ASH | a' | % | 6.84
7) TOTAL |  | % | 100
D. ULTIMATE ANALYSIS (AS FIRED BASIS)
1) CARBON | C | % | 68.4375
2) HYDROGEN | H | % | 3.948
3) OXYGEN | O | % | 7.6177
4) NITROGEN | N | % | 0.8609
5) SULPHUR | S | % | 0.14783
6) ASH | am | % | 5.9481
7) MOISTURE | mfc | % | 13.04
8) TOTAL |  | % | 100
E. HIGHER HEATING VALUE
1) H.H.V (AIR DRY BASIS) | Hf | Kcal/kg | 6890
2) SURFACE MOISTURE | Sm | % | 8.3
3) H.H.V (AS FIRED BASIS) | Hfc | Kcal/kg | Hfc = Hf*(100-Sm)/100
6318.1
2. COAL CONSUMPTION | Wfe | kg/hr | 24350
Ⅱ. REFUSE ANALYSIS
LOAD |  |  | #2 BLR 100%(225T/H)
DATE |  |  | 2007. 6. 09.(O/H전 성능시험)
TIME |  |  | 09:30~11:30
FUEL |  |  | 중국 Shenhua Coal
ITEM | SYMBOL | UNIT | RESULT | 비 고
1. UNBURNED CARBON ANALYSIS
A. REFUSE DISTRIBUTION RATE
1) ASH PIT | Rp | % | 10
2) ECO. HOPPER | Re | % | 0
3) AH HOPPER | Ra | % | 0
4) EP HOPPER | Rd | % | 90
B. UNBURNED CARBON RATE
1) ASH PIT | Up | % | 28.77
2) ECO. HOPPER | Ue | % | 13.84
3) AH HOPPER | Ua | % | 0
4) EP HOPPER | Ud | % | 4.69
C. UNBURNED CARBON RATE/ | U | % | U = 1/100(RpUp+ReUe+RaUa+RdUd)
DRY REFUSE |  |  | 7.1
D. ASH CONTENT | am | % | 5.9481
E. TOTAL DRY REFUSE / | Wd'p' | kg/kg.F | Wd'p' = am/(100-U)
AS FIRED FUEL |  |  | 0.064
2. UNBURNED CARBON / | Cu | kg/kg.F | Cu = Wd'p'*U/100
AS FIRED FUEL |  |  | 0.0045
3. BURNED CARBON / | Cb | kg/kg.F | Cb = C/100-Cu
AS FIRED FUEL |  |  | 0.6799
Ⅲ. BOILER EFFICIENCY CALCULATION
TEST UNIT & LOAD |  |  | #2 BLR 100%(225T/H)
DATE |  |  | 2007. 6. 09.(O/H전 성능시험)
TIME |  |  | 09:30~11:30
FUEL |  |  | 중국 Shenhua Coal
ITEM | SYMBOL | UNIT | RESULT | 비 고
1. AIR TEMPERATURE
1) AMBIENT AIR | tA | ℃ | 21.5556
2) FDF OUT AIR | tA6 | ℃ | 45.4667
3) GAH OUT AIR | tA9 | ℃ | 343.6444
4) REFERENCE AIR | tRA | ℃ | 45.4667
5) REFERENCE AIR (DESIGN) | tRAD | ℃ | 32
6) A/H INLET AIR (DESIGN) | tA8D | ℃ | 32
7) A/H INLET PRIMARNY AIR (A) | tA8pa-A | ℃ | 45.4667
8) A/H INLET PRIMARNY AIR (B) | tA8pa-B | ℃ | 45.4667
9) A/H INLET PRIMARNY AIR (AVE) | tA8pa | ℃ | 45.4667
10) A/H INLET SECONDARY AIR (A) | tA8sa-A | ℃ | 45.4667
11) A/H INLET SECONDARY AIR (B) | tA8sa-B | ℃ | 45.4667
12) A/H INLET SECONDARY AIR(AVE) | tA8sa | ℃ | 45.4667
13) PRIMARY AIR WEIGHT AT | Wpa | % | 0
A/H INLET
14) SECONDARY AIR WEIGHT AT | Wsa | % | 100
A/H INLET
15) WEIGHTED AVERAGE | tA8 | tA8 = (Wpa*tA8pa+Wsa*tA8sa)/(Wpa+Wsa)
AH INLET AIR |  | ℃ | 45.4667
2. GAS TEMPERATURE
1) A/H IN GAS (A) | tG14-A | ℃ | 381.7444
2) A/H IN GAS (B) | tG14-B | ℃ | 381.7444
3) A/H IN GAS (AVE) | tG14 | ℃ | 381.7444
4) A/H OUT GAS (A) | tG15-A | ℃ | 154.2593
5) A/H OUT GAS (B) | tG15-B | ℃ | 154.2593
6) A/H OUT GAS (AVE) | tG15 | ℃ | 154.2593
ITEM | SYMBOL | UNIT | RESULT | 비 고
3. MOISTURE IN AIR
1) DRY BULB TEMP. | tA | ℃ | 21.5556
2) WET BULB TEMP. | tW | ℃ | 15.8889
3) RELATIVE HUMIDITY | Ø | % | 54.2222
4) ATMOS. PRESS | PA | mmHg | 760
5) SAT. PRESS AT tA | Ps | mmHg | 19.2
6) PARTIAL PRESS OF VAPOR | PmA | mmHg | PmA = Ø*Ps/100
IN WET AIR |  |  | 10.41
7) MOIST IN DRY AIR | WmA' | kg/kgAIR | WmA' = 0.622*PmA/(PA-PmA)
0.0086
4. A/H INLET GAS ANALYSIS
1) O2(A) | O2-A | % | 3.15
2) O2(B) | O2-B | % | 3.15
3) O2(AVE) | O2 | % | 3.15
4) CO2(A) | CO2-A | % | 16.6 | ##
5) CO2(B) | CO2-B | % | 16.6
6) CO2(AVE) | CO2 | % | 16.6
7) N2 | N2 | % | N2 = 100 - (O2 + CO2)
80.25
5. A/H OUT GAS ANALYSIS
1) O2(A) | O2'-A | % | 4.4
2) O2(B) | O2'-B | % | 4.4
3) O2(AVE) | O2' | % | 4.4
4) CO2(A) | CO2'-A | % | 15.65 | ##
5) CO2(B) | CO2'-B | % | 15.65
6) CO2(AVE) | CO2' | % | 15.65
7) N2 | N2' | % | N2' = 100 - (O2 '+ CO2')
79.95
6. DRY GAS WEIGHT
1) A/H INLET GAS | WG'14 | WG'=[(44.01*CO2+32.0*O2+28.02*N2
+28.01*CO)/(12.01*(CO2+CO))]
*[Cb+(12.01*S/100)/32.07]
|  | kg/kg.F | 10.512
2) A/H OUTLET GAS | WG'15 | kg/kg.F | 11.113
ITEM | SYMBOL | UNIT | RESULT | 비 고
7. N2 WEIGHT
1) A/H INLET GAS | WG'14N2 | kg/kg.F | WG'N2=28.02*N2/(12.01*(CO2+CO))
*(Cb+12.01*S/(100*32.07)
7.675
2) A/H OUTLET GAS | WG'15N2 | kg/kg.F | 8.11
8. DRY AIR WEIGHT
1) A/H OUTLET GAS | WA'9 | kg/kg.F | WA' = (WG'N2-N/100)/0.7685
9.976
2) A/H INLET GAS | WA'8 | kg/kg.F | 10.542
9. MOSIT. IN AH INLET GAS | WmG14 | WmG14 = 8.936*H/100+WmA'*WA'9+mf/100
|  | kg/kg.F | 0.569
10. MOSIT. IN AH OUTLET GAS | WmG15 | WmG15 = WmG14+(WG'15-WG'14)*WmA'
|  | kg/kg.F | 0.574
11. AH LEAKAGE RATIO | AL | AL = [(WG'15+WmG15)-(WG'14+WmG14)]/
(WG'14+WmG14)*100
|  | % | 5.469
12. EXCESS AIR
1) THEORETICAL AIR | Aθ | Aθ=[11.51*Cb+[34.30*(H-O/7.937)
+4.335*S]/100
|  | kg/kg.F | 8.857
2) EXCESS AIR | Ax | % | Ax = [(WA'9-Aθ)/Aθ]*100
(ECO. OUT BASE) |  |  | 12.63
13. HEAT LOSS CALCULATION
1) ATMOS. PRESS. | PA | ata | 1.0332
2) PARTIAL PRESS. OF VAPOR | PmG | PmG = PA/[1+(100*1.5*Cb)/(WmG15
IN FLUE GAS |  | *(CO2+CO))]
|  | ata | 0.084
3) STM ENTHALPY AT tG15 & PmG | h15 | Kcal/kg | 654.32 | ##
4) SAT.STM ENTHALPY AT tRA | hRv | Kcal/kg | 617.22
5) SAT.WTR ENTHALPY AT tRA | hRw | Kcal/kg | 46.484
6) SPEC HEAT @tG15 & tRA | CPG' | Kcal/kg | 0.239
7) DESIGN RADIATION LOSS | Lβ' | % | 0.31
8) DESIGN UNMEASURED LOSS | Lum' | % | 0.5
ITEM | SYMBOL | UNIT | RESULT | 비 고
14. HEAT LOSSES
1) DRY GAS LOSS | LG' | Kcal/kg | LG' = WG'15*CPG'*(tG15-tRA)
|  |  | 288.95 | ##
2) MOIST IN FUEL LOSS | Lmf | Kcal/kg | Lmf = (mfc/100)*(h15-hRw)
79.26
3) MOISTURE FROM BURNING | LH | Kcal/kg | LH = 8.936*(H/100)*(h15-hRw)
OF HYDROGEN LOSS |  |  | 214.44
4) ATOMIZING STEAM LOSS | Lz | Kcal/kg | Lz = (Wze/Wfe)*(h15-hRv)
0
5) MOIST IN AIR LOSS | LmA | Kcal/kg | LmA = WmA'*WA'8*(h15-hRv)
3.36
6) RADIATION LOSS | Lβ | Lβ= DESIGN RAD. LOSS(Lβ')*Hfc/100
|  | Kcal/kg | 19.59
7) UNBURNED CARBON LOSS | Luc | Kcal/kg | Luc = 8100*Cu
|  |  | 36.45 | ##
8) UNMEASURED LOSS | Lum | Kcal/kg | Lum = DESIGN Lum'(%)*Hfc/100
31.59
9) TOTAL LOSS | L | L = LG'+Lmf+LH+Lz+LmA+Lβ+Luc+Lum
|  | Kcal/kg | 673.64
15. HHV OF FUEL | Hfc | Kcal/kg | 6318.1
16. HEAT CREDIT CALCULATION DATA
1) SPEC. HEAT OF AIR | cpA' | Kcal/kg℃ | 0.24
2) SPEC. HEAT OF OIL | cpO | Kcal/kg℃ | -
3) SPEC. HEAT OF COAL | cpC | Kcal/kg℃ | -
4) SPEC. HEAT OF STEAM | cpS | Kcal/kg℃ | 0.45
5) ATOM. STM ENTHALPY | hz. | Kcal/kg℃ | -
6) AUX. DRIVER POWER | kwh | KW | 485.22
CONSUMPTION
7) DRIVER EFFICIENCY | ηx | - | 0.9
ITEM | SYMBOL | UNIT | RESULT | 비 고
17. HEAT CREDITS
1) HEAT IN ENTERING AIR | BA | Kcal/kg.F | BA = WA'8*cpA'*(tA8-tRA)
0
2) HEAT IN ATOMIZING STEAM | Bz | Kcal/kg.F | Bz = x*(hz-hRv)
0
3) SENSIBLE HEAT IN FUEL | Bf | Kcal/kg.F | Bf = cpO*(tfo-tRA)
0
4) HEAT SUPPLIED BY | Bx | Kcal/kg.F | Bx = (860*kWh*ηx)/Wfe
AUX. DRIVERS |  |  | 15.42
5) HEAT SUPPLIED BY | BmA | Kcal/kg.F | BmA = WmA'*WA'8*cpS*(tA8-tRA)
MOISTURE IN AIR |  |  | 0
6) TOTAL | B | Kcal/kg.F | 15.42
18. HEAT LOSS PERCENTAGE
1) DRY GAS LOSS | LG'(%) | % | LG'(%) = LG'*100/(Hfc+B)
4.5622
2) MOISTURE IN FUEL LOSS | Lmf(%) | % | Lmf(%) = LmF*100/(Hfc+B)
1.25
3) MOISTURE FROM BURNING | LH(%) | % | LH(%) = LH*100/(Hfc+B)
OF HYDROGEN LOSS |  |  | 3.39
4) MOIST. IN AIR LOSS | LmA(%) | % | LmA(%) = LmA*100/(Hfc+B)
0.05
5) RADIATION LOSS | Lβ(%) | % | Lβ(%) = Lβ*100/(Hfc+B)
0.31
6) UNBURNED CARBON LOSS | Luc(%) | % | Luc(%) = Luc*100/(Hfc+B)
0.58
7) UNMEASURED LOSS | Lum(%) | % | Lum(%) = Lum*100/(Hfc+B)
0.5
8) TOTAL LOSS | L(%) | % | 10.6422
19. MEASURED BOILER EFFICIENCY | ηm | % | ηm = 100-L(%)
89.36
20. DESIGN BLR EFFICIENCY | ηD | % | 88.38
21. EFFICIENCY DEVIATION | Δη | % | ηm = ηm-ηD
0.98
EFFICIENCY CORRECTION for
GUARANTEE CONDITION |  |  |  | 0
ITEM | SYMBOL | UNIT | RESULT | 비 고
22. HEAT CREDIT CORRECTION (FOR REFERENCE AIR TEMP.)
1) HEAT IN ENTERING AIR | ΔBA | Kcal/kg.F | ΔBA = WA'8*CPA'(tRAD-tRA)
-34.07
2) HEAT IN ATOMIZING STEAM | ΔBz | Kcal/kg.F | ΔBz = (Wze/wfe)*(tRAD-tRA)
0
3) SENSIBLE HEAT IN FUEL | ΔBf | Kcal/kg.F | ΔBf = CPO*(tRAD-tRA)
0
4) HEAT SUPPLIED BY | ΔBmA | Kcal/kg.F | ΔBmA=WmA'*WA'8*cpS*(tRAD-tRA)
MOIST IN AIR |  |  | -0.55
5) TOTAL | ΔB | Kcal/kg.F | -34.62
23. HEAT LOSS CORRECTION DATA
1) C/H RATIO | C/H | - | C/H=Carbon WT%/Hydrogen WT%
17.33
2) MOIST. IN FUEL , DESIGN | mfD | % | 9
3) H2 IN FUEL , DESIGN | HD | % | 4.4
4) MOIST. IN AIR , DESIGN | WmA'D | kg/kg AIR | 0.014
5) CORRECTED GAS TEMP. | tG15δ | ℃ | tG15δ=[tA8D*(tG14-tG15)+tG14*
(A/H OUTLET) |  |  | (tG15-tA8)]/(tG14-tA8)
145.15
6) STM ENTHALPY AT tG15δ,PmG | h15δ | Kcal/kg | 654.32
7) SAT. STM ENTHALPY AT | hRVD | Kcal/kg | 611.44
DESIGN REF. AIR TEMP.
8) SAT. WATER ENTHALPY | hRwD | Kcal/kg | 32.01
AT DESIGN REF. TEMP.
9) SPEC HEAT OF GAS(WET BASE) | CPG | Kcal/kg℃ | 0.246
ITEM | SYMBOL | UNIT | RESULT | 비 고
24. HEAT LOSS CORRECTION
A. FOR REFERENCE AIR TEMP.
1) DRY GAS LOSS CORRECTION | ΔLG' | Kcal/kg.F | ΔLG'=WG'15*CPG'*[(tG15δ-tRAD)
-(tG15-tRA)]
11.57
2) MOISTURE IN FUEL LOSS | ΔLmf1 | Kcal/kg.F | ΔLmF1=(mfc/100)*[(h15δ-hRwD)
CORRECTION |  |  | -(h15-hRw)
1.89
3) MOISTURE FROM BURNING OF | ΔLH1 | ΔLmF1=8.936*(H/100)*[(h15δ-hRwD)
HYDROGEN LOSS CORRECTION |  | -(h15-hRw)]
|  | Kcal/kg.F | 5.11
4) MOISTURE IN AIR LOSS | ΔLmA1 | Kcal/kg.F | ΔLmA1=WmA'*WA'8*[(h15δ-hRwD)
CORRECTION |  |  | -(h15-hRw)]
0.52
5) ATOMIZING STEAM LOSS | ΔLz | Kcal/kg.F | ΔLz=x*[(h15δ-hRwD)-(h15-hRv)]
CORRECTION |  |  | 0
B. FOR H2 IN FUEL
1) MOISTURE IN FUEL LOSS | ΔLmf2 | ΔLmf2 = [(mfD-mfc)/100]*(h15δ-hRwD)
CORRECTION |  | Kcal/kg | -25.14
2) MOISTURE FROM BURNING | ΔLH2 | ΔLH2 = [8.936(HD-H)/100]*(h15δ-hRwD)
OF HYDROGEN CORRECTION |  | Kcal/kg | 25.14
C. FOR MOISTURE IN AIR
1) MOISTURE IN AIR LOSS | ΔLmA2 | ΔLmA2 = (WmA'D-WmA')*WA'8*(h15δ-hRwD)
CORRECTION |  | Kcal/kg | 2.44
D. GROSS CALORIFIC VALUE | ΔLHHV | % | 0.27 | ΔLHHV(%)= (Hfc-
CORRECTION |  |  |  | HfcD)*(-0.5/400)
←KUMI #1 80%
E. ECO.INLET FEED WATER TEMP. | ΔLFw | % | -0.02 | ΔLFw(%)= (FwT-
CORRECTION |  |  |  | FwTD)*(0.12/40)
←KUMI #1 80%
F. TOTAL CORRECTION | ΔL | Kcal/kg | 21.53
25. CORRECTED BOILER EFFICIENCY | ηc | ηc=[1-(L+ΔL)/(Hfm+B-ΔB)]+ΔLHHV+ ΔLFw
0 |  | % | 89.33
*. EFFICIENCY CORRECTION | Δηc | % | -0.03 | Δηc = ηc-ηm
26. DESIGN BLR EFFICIENCY | ηD | % | 88.38
27. EFFICIENCY DEVIATION | Δη | % | 0.95 | Δη = ηc-ηD
IV. CO2 CALCULATION (VOL % , DRY)
ITEM | SYMBOL | UNIT | RESULT | 비 고
1. COAL ANALYSIS (AS FIRED BASIS) |  |  |  | 0
1) CARBON | C | kg/kg.F | 0.68438
2) HYDROGEN | H | kg/kg.F | 0.03948
3) OXYGEN | O | kg/kg.F | 0.076177
4) NITROGEN | N | kg/kg.F | 0.008609
5) SULPHUR | S | kg/kg.F | 0.0014783
6) ASH | am | kg/kg.F | 0.059481
7) MOISTURE | mfc | kg/kg.F | 0.1304
8) TOTAL |  | kg/kg.F | 1
2. BURNED CARBON / AS FIRED FUEL | Cb | kg/kg.F | 0.6799
3. CO2 VOL % AT THE AH INLET
1) O2 | O2 | % | 3.15
2) THEORETICAL DRY AIR | TDA | TDA = 11.51*Cb+34.3*(H-O/7.937)+4.335*S
|  | kg/kg.F | 8.857
3) EXCESS AIR | Ax | Ax = 100*{(O2/100)*(31.32*Cb+11.528*S+
13.443*N+10.331*TDA)/[TDA*(2.73-
13.068*O2/100)]}
|  | kg/kg.F | 17.324
4) CO2 VOL%,DRY | CO2 | CO2' = 100*{(31.32*Cb+11.528*S)/[31.32
*Cb+11.528*S+13.443*N+TDA*(10.331+
(incl. SO2) |  | 13.068*Ax'/100)]}
|  | % | 16.0261
4. CO2 VOL % AT THE AH OUTLET
1) O2 | O2' | % | 4.4
2) THEORETICAL DRY AIR | TDA' | TDA' = 11.51*Cb+34.3*(H-O/7.937)+4.335*S
|  | kg/kg.F | 8.86
3) EXCESS AIR | Ax' | Ax' = 100*{(O2/100)*(31.32*Cb+11.528*S+
13.443*N+10.331*TDA)/[TDA*(2.73-
13.068*O2/100)]}
|  | kg/kg.F | 26.0241
4) CO2 VOL%,DRY | CO2' | CO2' = 100*{(31.32*Cb+11.528*S)/[31.32
*Cb+11.528*S+13.443*N+TDA*(10.331+
(incl. SO2) |  | 13.068*Ax'/100)]}
|  | % | 14.8979
| 공기예열기 성능시험 결과 계산 |  |  | 0
LOAD |  |  | #2 BLR 100%(225T/H)
DATE |  |  | 2007. 6. 09.(O/H전 성능시험)
TIME |  |  | 09:30~11:30
FUEL |  |  | 중국 Shenhua Coal
ITEM | SYMBOL | UNIT | RESULT | 비 고
1. GAS SIDE EFFICIENCY
1) GAH IN AIR TEMP. | tA8 | ℃ | 45.4667
2) GAH OUT AIR TEMP. | tA9 | ℃ | 343.6444
3) GAH IN GAS TEMP. | tG14 | ℃ | 381.7444
4) GAH OUT GAS TEMP(measured) | tG15 | ℃ | 154.2593
5) GAH OUT GAS TEMP. | tG15[NL] | ℃ | tG15[NL] = tG15 + (WA[L]*CPA
(NO - leakage) |  |  | *(tG15-tA8)/(100*CPG))
160.06
6) CORRECTED EFFICIENCY | ηG | % | ηG = (tG14-tG15[NL]*100/
(tG14-tA8)
65.92
2. X - RATIO
1) GAH IN GAS TEMP. | tG14 | ℃ | 381.7444
2) GAH OUT GAS TEMP. | tG15[NL] | ℃ | 160.06
(NO - leakage)
3) GAH OUT AIR TEMP. | tA9 | ℃ | 343.6444
4) GAH IN AIR TEMP. | tA8 | ℃ | 45.4667
5) X - RATIO | X | X = (tG14-tG15[NL])/(tA9-tA8)
0.74
3. 열 회수율
1) GAH 열 회수량 | Qhr | kcal/kg.F | Qhr={WG'14*CPG'*(tG14-tG15)}+
{WmG14*0.45*(tG14-tG15)}+
{0.2*Wd'14*(tG14-tG15)}-
{0.245*WA[L]*(tG15-tA8)}
1091.89
2) 연료 발열량 | Hfc | kcal/kg | 6318.1
3) GAH 열 회수율 | Rhr | % | Rhr = (Qhr*100)/Hfc
17.28
ITEM | SYMBOL | UNIT | RESULT
4. 과잉 공기율
1) GAH 입구 과잉공기율 | m₁ | - | m = (21*N2)/(21*N2-79*O2)
1.173
2) GAH 출구 과잉공기율 | m₂ | - | 1.261
5. 열 관류율
1) 전열량 | Q | kcal/hr | Q = Qhr * Wfe
26587521.5001
2) 전열면적 | A | ㎡ | 8590
3) LMTD | tm | ℃ | Δtm={(tG14-tA9)-(tG15[NL] -
tA8)} / ln{(tG14-tA9) /
(tG15[NL] - tA8)}
69.47
4) 열 관류율 | K | kcal | K = Q / (A * tm)
/㎡h℃
44.55
6. GAH LEAKAGE
1) DRY GAS ECO. OUT | WG'14 | kg/kg.F | 10.512
2) MOIST.IN ECO.OUT GAS | WmG14 | kg/kg.F | 0.569
3) WET GAS ECO.OUT | WG14 | kg/kg.F | WG14 = WG'14 + WmG14
11.081
4) DRY GAS GAH OUT | WG'15 | kg/kg.F | 11.113
5) MOIST.IN GAH OUT GAS | WmG15 | kg/kg.F | 0.574
6) WET GAS GAH OUT | WG15 | kg/kg.F | WG15 = WG'15 + WmG15
11.687
7) GAH LEAKAGE RATIO | A[L] | % | A[L] = (WG15-WG14) / WG14
5.469
Note on E28: HP: 단위가 kg 이므로 TON과 혼돈하지 말것
Note on E31: HP: ECO HOPPER와 ASH PIT를 포함한 값으로 ECO HOPPER 에서 SAMPLING하여 적용
Note on E39: HP: EP HOPPER 1 FIELD LEFT,RIGHT UBC AVERAGE
Note on E44: HP: 실측한 건구온도
Note on E45: HP: 15분 간격 LOGGING 값 평균
Note on E46: HP: 15분 간격 LOGGING 값 평균
Note on E50: HP: FDF OUTLET AIR TEMP 적용
Note on E59: HP: 15분 간격 LOGGING 값 평균
Note on E61: HP: 15분 간격 LOGGING 값 평균
Note on E64: HP: 15분 간격 실측값 평균
Note on E65: HP: 15분간격 실측값 평균
Note on E66: HP: 15분 간격 실측값 평균
Note on E68: HP: DRY BULB TEMP (E64)에 대한 포화증기 압력 : STM TABLE에서 확인
Note on E70: HP: 환경팀 ORSAT 분석치 평균값
Note on E72: HP: 환경팀 ORSAT 분석치 평균값
Note on E78: HP: 불변값(표준대기압)
Note on E83: HP: FDF OUT AIR TEMP (E45)값의 포화증기 엔탈피: STM TABLE 에서 확인
Note on E84: HP: FDF OUT AIR TEMP (E45) 값의 포화수 엔탈피 : STM TABLE 에서 확인
Note on E85: HP: 불변값
Note on E86: HP: 가변값 : BLR 부하별 DESIGN 값을 SPEC. (BLR취급설명서1권 12 PAGE)에서 찾아 적용
Note on E87: HP: 불변값
Note on E89: HP: 불변값
Note on E92: HP: 불변값
Note on E94: HP: 불변값
Note on E96: HP: 불변값
Note on E98: HP: 불변값: 성능탄 값
Note on E99: HP: 불변값
Note on E100: HP: 불변값
Note on E101: HP: 불변값
Note on E104: HP: STM TABLE
Note on E105: HP: 불변값: 32℃ 포화증기엔탈피
Note on E107: HP: 불변값: 32℃ 포화수엔탈피
Note on E109: HP: 불변값 : 0.246
Note on E110: HP: 불변값
Note on E111: HP: 기록지 15분 간격 logging값 평균
Note on E112: HP: 불변값
Note on E238: HP: 환경팀 오르자트 분석값 평균치
Note on E247: HP: 환경팀 오르자트 분석값 평균치

## 온도압력
보일러 성능시험 기록지 ( CCR : BCO2 )
시험 일시 |  | 2007 년 6 월 9 일 # 2 보일러 : 225 T/H
Ⅲ. 증기 및 급수온도 압력 ( 15분 간격 순시치 )
NO | 시각 | MAIN STM TEMP (℃) (TIR2013) | MAIN STM PR. (㎏/㎠) (PIR2012) | STM DRUM PR. (㎏/㎠) (PIR2028) | ECO IN WTR TEMP (℃) (TIR2009) | ECO OUT WTR TEMP (℃) (TIR2023) | FDF OUT AIR TEMP (℃) (TIR2015)
1 | 9:00 | 534 | 122.7 | 132.1 | 247.6 | 262.8 | 44.8
2 | 9:15 | 534 | 122.7 | 132.3 | 248.1 | 263.8 | 44.8
3 | 9:30 | 534 | 122.7 | 132.1 | 248 | 263.8 | 45
4 | 9:45 | 534 | 122.5 | 132.5 | 247.9 | 263.6 | 45.2
5 | 10:00 | 533 | 122.7 | 132.2 | 248.5 | 263.6 | 45.2
6 | 10:15 | 534 | 122.7 | 132.7 | 246.3 | 262.5 | 45.7
7 | 10:30 | 533 | 122.7 | 132.5 | 246.8 | 262.1 | 45.8
8 | 10:45 | 534 | 122.6 | 132.3 | 247.2 | 262.1 | 46.2
9 | 11:00 | 534 | 122.7 | 132.3 | 247 | 262.1 | 46.5
10
11
평균 |  | 533.7778 | 122.6667 | 132.3333 | 247.4889 | 262.9333 | 45.4667
Ⅳ. AIR & FLUE GAS | [13 empty] | 참고자료
NO | 시각 | GAH IN AIR TEMP (℃) (TI2107ABC) | GAH OUT AIR TEMP (℃) (TIR2110) | GAH IN GAS TEMP (℃) (TI2127) | GAH OUT GAS TEMP (℃) (TIR2132ABC) | O2 농도 ECO OUT (%) (AIC2128) | NOX 농도 (PPM) (AIR2139) | GAH IN AIR TEMP (℃) (TI 2107 A.B.C) |  |  | GAH OUT GAS TEMP (℃) (TIR 2132A.B.C) |  |  | GAH OUT GAS TEMP (℃) (LOCAL 실측)
1 | 9:00 | 43.6667 | 341.1 | 380 | 152.3333 | 2.78 | 319.3 | 46 | 39 | 46 | 155 | 151 | 151
2 | 9:15 | 43.6667 | 343 | 382.8 | 153.3333 | 2.78 | 303.7 | 46 | 39 | 46 | 156 | 152 | 152
3 | 9:30 | 43.6667 | 343.6 | 381.4 | 153.6667 | 2.84 | 321.2 | 46 | 39 | 46 | 156 | 152 | 153
4 | 9:45 | 44.3333 | 344 | 380.6 | 154 | 2.78 | 320.6 | 46 | 40 | 47 | 156 | 153 | 153
5 | 10:00 | 44.3333 | 344 | 381.3 | 154 | 2.84 | 315.6 | 46 | 40 | 47 | 156 | 153 | 153
6 | 10:15 | 44.3333 | 343.8 | 381.3 | 154.3333 | 2.71 | 318.7 | 46 | 40 | 47 | 157 | 153 | 153
7 | 10:30 | 44.6667 | 344 | 381.9 | 155 | 2.73 | 320.3 | 47 | 40 | 47 | 157 | 154 | 154
8 | 10:45 | 44.6667 | 344.3 | 380.8 | 155.3333 | 2.71 | 321.3 | 47 | 40 | 47 | 158 | 154 | 154
9 | 11:00 | 45.6667 | 345 | 385.6 | 156.3333 | 2.72 | 327.1 | 48 | 41 | 48 | 159 | 155 | 155
10
11
평균 |  | 44.3333 | 343.6444 | 381.7444 | 154.2593 | 2.7656 | 318.6444 | [6 empty] | 0 | 0 | 0
[14 empty] | 실측 평균 |  | 0
Note on E30: HP: CALCULATION SHEET 적용
Note on F16: HP: CALCULATION SHEET 적용
Note on F30: HP: CALCULATION SHEET 적용
Note on H16: HP: CALCULATION SHEET 적용
항목
항목

## 유량
보일러 성능시험 기록지 ( CCR : BCO2 )
시험 일시 |  | 2007 년 6 월 9 일
시험 항목 |  | # 2 보일러 : 225 T/H
시험 조건 |  | OAP 개도 (%) : 40 % , 운전 미분기 : A B C
Ⅰ. 유량 적산계 ( 시험 시작 및 종료 정시에 기록요 ) | [8 empty] | COAL FDR
NO | 시각 | MAIN STM FLOW (TON) (FQ2019) | FEED WTR FLOW (TON) (FQ2002) | SPRAY WTR FLOW (TON) (FQ2035) | CBD FLOW (TON) (FQ2029) | COAL FLOW (㎏) (FQ2210) | B-C 유 FLOW (℃) (FQ2302) |  | LOCAL 적산계 A (kg) | LOCAL 적산계 B (kg) | LOCAL 적산계 C (kg) | CCR 적산계 (TON) | CCR 순시값 (TON)
1 | 시작 9:00 | 25284166 | 353579 | N/A | 27967 | 2343772.9 | 204147.5 | 시작 9:00 | 131649852 | 128262799 | 107456634 | 2343772000 | 24.4
2 | 종료 11:00 | 25284615 | 354021 | N/A | 27967 | 2343821.6 | 204147.8 | 종료 11:00 | 131667739 | 128279758 | 107470047 | 2343821000 | 24.2
3 | 적산량 | 449 | 442 | N/A | 0 | 48.7 | 0.3 | 적산량 | 17887 | 16959 | 13413 | 49000 | 48.6
4 | 평균 | 224.5 | 221 | N/A | 0 | 24350 | 0.15 |  | 48259 |  |  | 49000 | -741
Ⅱ. 유량계 ( 15분 간격 순시치 )
NO | 시각 | MAIN STM FLOW (T/H) (FIR2019) | FEED WTR FLOW (T/H) (FIC2002) | SPRAY WTR FLOW (T/H) (FIR2035) | CBD FLOW (T/H) (FIR2029) | COAL FLOW (T/H) (FI2210ABC) | B-C 유 FLOW (T/H) (FIR2302)
1 | 9:00 | 224.4 | 221.5 | 11.9 | 0 | 24.4 | 0
2 | 9:15 | 226.8 | 224.9 | 12.4 | 0 | 24.4 | 0
3 | 9:30 | 223.9 | 219.2 | 12.3 | 0 | 24.3 | 0
4 | 9:45 | 224.2 | 221.7 | 12.1 | 0 | 24.3 | 0
5 | 10:00 | 225.3 | 223.2 | 12.3 | 0 | 24.4 | 0
6 | 10:15 | 224.5 | 221.2 | 12 | 0 | 24.3 | 0
7 | 10:30 | 224.8 | 221.4 | 11.4 | 0 | 24.3 | 0
8 | 10:45 | 226.4 | 221.7 | 11.8 | 0 | 24.2 | 0
9 | 11:00 | 224.4 | 220.4 | 10.6 | 0 | 24.2 | 0
10
11
평균 |  | 224.9667 | 221.6889 | 11.8667 | 0 | 24.3111 | "
Note on G10: HP: ton을 kg으로 환산 : calculation sheet에 kg 단위임
항목
항목

## 대기온도
보일러 성능시험 기록지 LOCAL #1
시험 일시 |  | 2007 년 6 월 9 일 # 2 보일러 : 225 T/H
Ⅲ. 대기온도 ( 15분 간격 순시치 )
NO | 시각 | 대기온도 (건구) (℃) | 대기온도 (습구) (℃) | 대기습도 (%) | 대기온도 (DIGITAL) (℃) | 대기습도 (DIGITAL) (%)
1 | 9:00 | 20 | 16 | 66
2 | 9:15 | 21 | 16 | 59
3 | 9:30 | 21 | 15 | 52 |  |  | 6
4 | 9:45 | 21 | 16 | 59 |  |  | 5
5 | 10:00 | 21 | 16 | 52 |  |  | 5
6 | 10:15 | 22 | 16 | 53 |  |  | 6
7 | 10:30 | 22 | 16 | 53 |  |  | 6
8 | 10:45 | 23 | 16 | 47 |  |  | 7
9 | 11:00 | 23 | 16 | 47 |  |  | 7
10
11
평균 |  | 21.5556 | 15.8889 | 54.2222 |  |  | 5.6667
비고
항목
DIGITAL 온도계 측정
: 건습구온도계 옆에
설치 참고용
건습구온도계 실측
: 바람이 통하지 않는
음지에 설치하여 측정

## O2CO2
보일러 성능시험 기록지 LOCAL #1
시험 일시 |  | 2007 년 3 월 29 일 # 3 보일러 : 145 T/H
* FLUE GAS ANALYSYS
NO |  | GAH INLET |  |  |  | GAH OUTLET
|  | ORSAT |  | 현장계측기 | CCR 계기 | ORSAT |  | TMS 계기
|  | CO2 | O2 | O2 | O2 | CO2 | O2 | O2
1 | 9:45 | 16.5 | 3.2 | 2.95 | 2.85
2 | 9:55 | 16.7 | 3.1 | 2.92 | 2.86
3 | 10:10 |  |  |  |  | 15.6 | 4.4 | 5.37
4 | 10:30 |  |  |  |  | 15.7 | 4.4 | 5.32
5
6
7
8
9
10
11
평균 |  | 16.6 | 3.15 | 2.935 | 2.855 | 15.65 | 4.4 | 5.345
비고
Note on C18: HP: CALCULATION SHEET 적용
Note on D18: HP: CALCULATION SHEET 적용
Note on G18: HP: CALCULATION SHEET 적용
Note on H18: HP: CALCULATION SHEET 적용
항목
시각

## 공업분석
분석일자 | 채취일자 | 시료번호 | 탄종 | 전수분 | 발열량 |  | 고유 수분 | 휘발분 | 고정탄소 | 회분 | 전유황분 | 분쇄도
[5 empty] | 건식 | 기건식
2007-03-05 | 2007-03-02 | 20070301 | CLARENCE COAL | 9.14 | 7200 | 7020 | 2.5 | 0 | 0 | 0 | 0.3 | 0
2007-03-05 | 2007-03-02 | 20070302 | SHENHUA | 13.48 | 7290 | 6890 | 5.6 | 0 | 0 | 0 | 0.26 | 0
2007-03-07 | 2007-03-05 | 20070303 | SHENHUA | 13.74 | 7290 | 6880 | 5.6 | 33.1 | 55.2 | 6.2 | 0.26 | 0
2007-03-07 | 2007-03-05 | 20070304 | CLARENCE COAL | 9.43 | 7200 | 7030 | 2.5 | 26.4 | 58.9 | 12.2 | 0.3 | 0
2007-03-07 | 2007-03-06 | 20070306 | SHENHUA | 13.46 | 7290 | 6890 | 5.6 | 0 | 0 | 0 | 0.26 | 0
2007-03-07 | 2007-03-06 | 20070305 | CLARENCE COAL | 9.26 | 7210 | 7030 | 2.5 | 0 | 0 | 0 | 0.3 | 0
2007-03-08 | 2007-03-07 | 20070307 | CLARENCE COAL | 9.42 | 7200 | 7020 | 2.5 | 0 | 0 | 0 | 0.31 | 0
2007-03-09 | 2007-03-08 | 20070309 | SHENHUA | 13.35 | 7290 | 6890 | 5.6 | 0 | 0 | 0 | 0.26 | 0
2007-03-12 | 2007-03-08 | 20070308 | CLARENCE COAL | 9.3 | 7190 | 7010 | 2.5 | 0 | 0 | 0 | 0.31 | 0
2007-03-12 | 2007-03-09 | 20070310 | SHENHUA | 13.91 | 7290 | 6880 | 5.6 | 0 | 0 | 0 | 0.27 | 0
2007-03-12 | 2007-03-09 | 20070311 | CLARENCE COAL | 9.74 | 7190 | 7010 | 2.4 | 0 | 0 | 0 | 0.31 | 0
2007-03-13 | 2007-03-12 | 20070312 | SHENHUA | 13.44 | 7280 | 6880 | 5.5 | 31.8 | 54.7 | 8 | 0.26 | 0
2007-03-13 | 2007-03-12 | 20070312 | CLARENCE COAL | 9.22 | 7200 | 7020 | 2.5 | 25.3 | 59.3 | 13 | 0.31 | 0
2007-03-14 | 2007-03-13 | 20070314 | SHENHUA | 13.41 | 7280 | 6880 | 5.5 | 0 | 0 | 0 | 0.27 | 0
2007-03-14 | 2007-03-13 | 20070315 | CLARENCE COAL | 9.21 | 7190 | 7020 | 2.5 | 0 | 0 | 0 | 0.31 | 0
2007-03-15 | 2007-03-14 | 20070316 | CLARENCE COAL | 9.1 | 7200 | 7020 | 2.5 | 0 | 0 | 0 | 0.32 | 0
2007-03-16 | 2007-03-15 | 20070318 | SHENHUA | 13.26 | 7280 | 6880 | 5.5 | 0 | 0 | 0 | 0.27 | 0
2007-03-16 | 2007-03-15 | 20070317 | CLARENCE COAL | 9.19 | 7200 | 7020 | 2.5 | 0 | 0 | 0 | 0.32 | 0
2007-03-19 | 2007-03-16 | 20070320 | CLARENCE COAL | 9.25 | 7190 | 7010 | 2.5 | 0 | 0 | 0 | 0.31 | 0
2007-03-19 | 2007-03-16 | 20070319 | SHENHUA | 13.13 | 7280 | 6880 | 5.5 | 0 | 0 | 0 | 0.26 | 0
2007-03-20 | 2007-03-19 | 20070322 | SHENHUA | 13.47 | 7290 | 6880 | 5.5 | 32.6 | 52.1 | 9.8 | 0.26 | 0
2007-03-20 | 2007-03-19 | 20070321 | CLARENCE COAL | 9.27 | 7200 | 7020 | 2.5 | 25.6 | 58 | 13.9 | 0.31 | 0
2007-03-22 | 2007-03-20 | 20070323 | SHENHUA | 13.55 | 7280 | 6880 | 5.6 | 0 | 0 | 0 | 0.26 | 0
2007-03-22 | 2007-03-20 | 20070324 | CLARENCE COAL | 9.36 | 7190 | 7020 | 2.5 | 0 | 0 | 0 | 0.31 | 0
2007-03-22 | 2007-03-21 | 20070325 | CLARENCE COAL | 9.18 | 7200 | 7020 | 2.5 | 0 | 0 | 0 | 0.31 | 0
2007-03-23 | 2007-03-22 | 20070327 | SHENHUA | 13.51 | 7290 | 6880 | 5.5 | 0 | 0 | 0 | 0.26 | 0
2007-03-26 | 2007-03-23 | 20070328 | SHENHUA | 13.62 | 7280 | 6880 | 5.5 | 32 | 54.5 | 8 | 0.27 | 0
2007-03-26 | 2007-03-23 | 20070329 | CLARENCE COAL | 9.43 | 7110 | 6930 | 2.5 | 25.3 | 59.3 | 12.9 | 0.41 | 0
2007-03-28 | 2007-03-26 | 20070330 | CLARENCE COAL | 9.28 | 7190 | 7010 | 2.5 | 25.4 | 59.4 | 12.8 | 0.31 | 0
2007-03-29 | 2007-03-28 | 20070331 | CLARENCE COAL | 9.43 | 7190 | 7020 | 2.5 | 0 | 0 | 0 | 0.3 | 0
2007-03-30 | 2007-03-29 | 20070332 | CLARENCE COAL | 9.13 | 7190 | 7020 | 2.5 | 0 | 0 | 0 | 0.3 | 0
2007-04-02 | 2007-03-30 | 20070333 | CLARENCE COAL | 9.19 | 7200 | 7020 | 2.5 | 0 | 0 | 0 | 0.31 | 0
2007-04-02 | 2007-03-31 | 20070334 | CLARENCE COAL | 9.2 | 7200 | 7020 | 2.5 | 0 | 0 | 0 | 0.32 | 0
유연탄 분석값